## Sheet1
LTDS 'Foundational' Data Summary Table - Interim version issued 2022-11-11
DNO licence area where typical grid instance model is located:
CIM class to be populated |  |  |  | DNO applications/databases/documents which are sources of data (specify per class or attribute, as appropriate) | issues identified with retrieval or translation of data from source
objects of class required to be created
| population required? | actual CIM object with attribute (may be parent class) | attribute name
BaseVoltage
one for each base voltage in LTDS modeling scope
| OPTIONAL | IdentifiedObject | description
| TOOL | IdentifiedObject | mRID
| REQUIRED | IdentifiedObject | name
| REQUIRED | BaseVoltage | nominalVoltage
BusbarSection
one for each bus that can be individually de-energized within LTDS modeling scope
| OPTIONAL | IdentifiedObject | description
| TOOL | IdentifiedObject | mRID
| REQUIRED | IdentifiedObject | name
| ON HOLD (SC) | BusbarSection | ipMax
Disconnector
per Switch population guidelines below
| OPTIONAL | IdentifiedObject | description
| TOOL | IdentifiedObject | mRID
| REQUIRED | IdentifiedObject | name
| REQUIRED | Switch | normalOpen
| REQUIRED | Switch | ratedCurrent
Breaker
per Switch population guidelines below
| OPTIONAL | IdentifiedObject | description
| TOOL | IdentifiedObject | mRID
| REQUIRED | IdentifiedObject | name
| REQUIRED | Switch | normalOpen
| REQUIRED | Switch | ratedCurrent
| REQUIRED | ProtectedSwitch | breakingCapacity
ACLineSegment
at least one for every line within LTDS modeling scope which connects between substations
(multiple ACLineSegments may be used to model sections of a line with different impedances)
('line' is essentially the same as the LTDS 'circuit')
| OPTIONAL | IdentifiedObject | description
| TOOL | IdentifiedObject | mRID
| REQUIRED | IdentifiedObject | name
| REQUIRED | Conductor | length
| ON HOLD (SC) | ACLineSegment | b0ch
| REQUIRED | ACLineSegment | bch
| ON HOLD (SC) | ACLineSegment | g0ch
| OPTIONAL | ACLineSegment | gch
| REQUIRED | ACLineSegment | r
| REQUIRED | ACLineSegment | r0
| ON HOLD (SC) | ACLineSegment | shortCircuitEndTemperature
| REQUIRED | ACLineSegment | x
| REQUIRED | ACLineSegment | x0
OperationalLimitSet (for ACLineSegment or other ConductingEquipment associated with circuit)
required for each ACLineSegment (optional for other ConductingEquipment associated with circuit); one for each timeframe; as many timeframes as desired may be defined such that the entire calendar year is covered
| OPTIONAL | IdentifiedObject | description
| TOOL | IdentifiedObject | mRID
| REQUIRED | IdentifiedObject | name
| REQUIRED | OperationalLimitSet | validFrom
| REQUIRED | OperationalLimitSet | validTo
CurrentLimit (for ACLineSegment or other ConductingEquipment associated with circuit)
one for each OperationalLimitSet
| OPTIONAL | IdentifiedObject | description
| TOOL | IdentifiedObject | mRID
| REQUIRED | IdentifiedObject | name
| REQUIRED | CurrentLimit | normalValue
OperationalLimitType (for ACLineSegment or other ConductingEquipment associated with circuit)
one
| OPTIONAL | IdentifiedObject | description
| TOOL | IdentifiedObject | mRID
| REQUIRED | IdentifiedObject | name
| REQUIRED | OperationalLimitType | direction (must=absoluteValue)
| REQUIRED | OperationalLimitType | isInfiniteDuration (must=true)
| REQUIRED | OperationalLimitType | kind (must=patl)
PowerTransformer
one for every transformer within LTDS modeling scope
| OPTIONAL | IdentifiedObject | description
| TOOL | IdentifiedObject | mRID
| REQUIRED | IdentifiedObject | name
| ON HOLD (SC) | PowerTransformer | beforeShCircuitHighestOperationCurrent
| ON HOLD (SC) | PowerTransformer | beforeShCircuitHighestOperationVoltage
| ON HOLD (SC) | PowerTransformer | beforeShortCircuitAnglePf
| ON HOLD (SC) | PowerTransformer | highSideMinOperatingU
| ON HOLD (SC) | PowerTransformer | isPartOfGeneratorUnit
| ON HOLD (SC) | PowerTransformer | operationalValuesConsidered
| REQUIRED | PowerTransformer | reverseFlowCapability
PowerTransformerEnd
one for every winding of each transformer within LTDS modeling scope
| OPTIONAL | IdentifiedObject | description
| TOOL | IdentifiedObject | mRID
| REQUIRED | IdentifiedObject | name
| REQUIRED | TransformerEnd | endNumber
| ON HOLD (SC) | TransformerEnd | grounded
| ON HOLD (SC) | TransformerEnd | rground
| ON HOLD (SC) | TransformerEnd | xground
| REQUIRED | TransformerEnd | earthingMethod
| REQUIRED | PowerTransformerEnd | b
| ON HOLD (SC) | PowerTransformerEnd | b0
| REQUIRED | PowerTransformerEnd | connectionKind
| OPTIONAL | PowerTransformerEnd | g
| ON HOLD (SC) | PowerTransformerEnd | g0
| REQUIRED | PowerTransformerEnd | phaseAngleClock
| REQUIRED | PowerTransformerEnd | r
| ON HOLD (SC) | PowerTransformerEnd | r0
| REQUIRED | PowerTransformerEnd | ratedS
| REQUIRED | PowerTransformerEnd | ratedU
| REQUIRED | PowerTransformerEnd | x
| REQUIRED | PowerTransformerEnd | x0
OperationalLimitSet
one for each high winding of 2-winding transformer, one for each winding of 3-winding transformer
| OPTIONAL | IdentifiedObject | description
| TOOL | IdentifiedObject | mRID
| REQUIRED | IdentifiedObject | name
ApparentPowerLimit (for normal direction flow for PowerTransformer)
one for each OperationalLimitSet, reflects ONAN rating reduced as necessary to reflect DNO operating practice (to manage aging, for example)
| OPTIONAL | IdentifiedObject | description
| TOOL | IdentifiedObject | mRID
| REQUIRED | IdentifiedObject | name
| REQUIRED | CurrentLimit | normalValue
ApparentPowerLimit (for reverse direction flow for PowerTransformer)
one for each OperationalLimiSet associated with transformer high winding where PowerTransformer.reverseFlowCapability=differentFromNormal
| OPTIONAL | IdentifiedObject | description
| TOOL | IdentifiedObject | mRID
| REQUIRED | IdentifiedObject | name
| REQUIRED | CurrentLimit | normalValue
OperationalLimitType (for PowerTransformer)
two: one for normal flow limits, one for reverse flow limits
| OPTIONAL | IdentifiedObject | description
| TOOL | IdentifiedObject | mRID
| REQUIRED | IdentifiedObject | name
| REQUIRED | OperationalLimitType | direction (must=high)
| REQUIRED | OperationalLimitType | isInfiniteDuration (must=true)
| REQUIRED | OperationalLimitType | kind (must=patl)
| OPTIONAL | OperationalLimitType | transformerReverseFlow (must=true for reverse flow limit)
RatioTapChanger
one for each tap changer on transformer within LTDS modeling scope
| OPTIONAL | IdentifiedObject | description
| TOOL | IdentifiedObject | mRID
| REQUIRED | IdentifiedObject | name
| REQUIRED | TapChanger | highStep
| REQUIRED | TapChanger | lowStep
| REQUIRED | TapChanger | ltcFlag
| REQUIRED | TapChanger | neutralStep
| REQUIRED | TapChanger | neutralU
| REQUIRED | TapChanger | normalStep
| REQUIRED | RatioTapChanger | stepVoltageIncrement
TapChangerControl
one for each tap changer with .ltcFlag=true
| OPTIONAL | IdentifiedObject | description
| TOOL | IdentifiedObject | mRID
| REQUIRED | IdentifiedObject | name
| REQUIRED | RegulatingControl | mode (must=voltage)
LinearShuntCompensator
either a LinearShuntCompensator or NonLinearShuntCompensator must be populated for each shunt compensator within LTDS modeling scope
| OPTIONAL | IdentifiedObject | description
| TOOL | IdentifiedObject | mRID
| REQUIRED | IdentifiedObject | name
| OPTIONAL | ShuntCompensator | aVRDelay
| OPTIONAL | ShuntCompensator | grounded
| REQUIRED | ShuntCompensator | maximumSections
| REQUIRED | ShuntCompensator | nomU
| REQUIRED | ShuntCompensator | normalSections
| OPTIONAL | ShuntCompensator | voltageSensitivity
| ON HOLD (SC) | LinearShuntCompensator | b0PerSection
| REQUIRED | LinearShuntCompensator | bPerSection
| ON HOLD (SC) | LinearShuntCompensator | g0PerSection
| REQUIRED | LinearShuntCompensator | gPerSection
NonLinearShuntCompensator
either a LinearShuntCompensator or NonLinearShuntCompensator must be populated for each shunt compensator within LTDS modeling scope
| OPTIONAL | IdentifiedObject | description
| TOOL | IdentifiedObject | mRID
| REQUIRED | IdentifiedObject | name
| OPTIONAL | ShuntCompensator | aVRDelay
| OPTIONAL | ShuntCompensator | grounded
| REQUIRED | ShuntCompensator | maximumSections
| REQUIRED | ShuntCompensator | nomU
| REQUIRED | ShuntCompensator | normalSections
| OPTIONAL | ShuntCompensator | voltageSensitivity
NonLinearShuntCompensatorPoint
as required for every NonLinearShuntCompensator
| REQUIRED | NonLinearShuntCompensatorPoint | b
| ON HOLD (SC) | NonLinearShuntCompensatorPoint | b0
| REQUIRED | NonLinearShuntCompensatorPoint | g
| ON HOLD (SC) | NonLinearShuntCompensatorPoint | g0
| REQUIRED | NonLinearShuntCompensatorPoint | sectionNumber
RegulatingControl
one for each LinearShuntCompensator or NonLinearShuntCompensator
| OPTIONAL | IdentifiedObject | description
| TOOL | IdentifiedObject | mRID
| REQUIRED | IdentifiedObject | name
| REQUIRED | RegulatingControl | mode
StaticVarCompensator
one for each static VAr compensator within LTDS modeling scope
| OPTIONAL | IdentifiedObject | description
| TOOL | IdentifiedObject | mRID
| REQUIRED | IdentifiedObject | name
| REQUIRED | StaticVarCompensator | capacitiveRating
| REQUIRED | StaticVarCompensator | inductiveRating
| REQUIRED | StaticVarCompensator | slope
| OPTIONAL | StaticVarCompensator | sVCControlMode
| OPTIONAL | StaticVarCompensator | voltageSetPoint
VoltageLevel
every ConductingEquipment child except Power Transformer is contained in either Line or VoltageLevel using the Equipment.EquipmentContainer association
| OPTIONAL | IdentifiedObject | description
| TOOL | IdentifiedObject | mRID
| REQUIRED | IdentifiedObject | name
Substation
every PowerTransformer is contained in either a Substation or Line using the Equipment.EquipmentContainer association
| OPTIONAL | IdentifiedObject | description
| TOOL | IdentifiedObject | mRID
| REQUIRED | IdentifiedObject | name
Line
every ConductingEquipment child except Power Transformer is contained in either Line or VoltageLevel using the Equipment.EquipmentContainer association
optionally ConductingEquipment contained in a VoltageLevel or Substation may use the Equipment.AdditionalEquipmentContainer association to be contained in Line
| OPTIONAL | IdentifiedObject | description
| TOOL | IdentifiedObject | mRID
| REQUIRED | IdentifiedObject | name
Location
one Location with at least 2 PositionPoints for each ACLineSegment
one Location with a single PositionPoint for each ConductingEquipment of a type other than ACLineSegment
one Location with one or more PositionPoints for every Substation
| OPTIONAL | IdentifiedObject | description
| TOOL | IdentifiedObject | mRID
| REQUIRED | IdentifiedObject | name
CoordinateSystem
one for the licence area
| OPTIONAL | IdentifiedObject | description
| TOOL | IdentifiedObject | mRID
| REQUIRED | IdentifiedObject | name
| REQUIRED | CoordinateSystem | crsUrn (must=urn:ogc:def:crs:EPSG::4326)
PositionPoint
as necessary to meet requirements for Locations described above
| REQUIRED | PositionPoint | sequenceNumber
| REQUIRED | PositionPoint | xPosition
| REQUIRED | PositionPoint | yPosition
| OPTIONAL | PositionPoint | zPosition
KEY
| REQUIRED | attribute must be populated
| OPTIONAL | attribute may have to be populated - specific rules are being captured in the LTDS Modelling Guide
| ON HOLD (SC) | attribute population requirement dependent on short circuit input data decision
| TOOL | attribute is populated and maintained (to be persistent) by the tool used to produce LTDS modeling
| green text | changed since previous version of LTDS Foundation Data Summary Table
Switch population guidelines
switches (represented either by Breakers or Disconnectors as appropriate) need to be modeled such that:
every ConductingEquipment instance other than ACLineSegments can be cleared (or isolated) using switches
every line (which could be one ACLineSegment or a series of ACLineSegments) can be cleared using switches
LTDS modeling scope
scope of grid model is from Subtransmission to the HV bus in Primary substations plus any HV circuits interconnecting Primary substations