## Key
Class | Parent Class or Class | Attribute | Description (CIM Notes) | LTDS Profile | LTDS UML Constraint | LTDS Additional Constraints | In CGMES 3.0 profile | <CIM standard profile name and edition> | In CIM information model | Comments / Questions | Existing LTDS requirement | Proposed GC0139 requirement
Instance Requirements |  |  | General philosophy: <summary of data content requirements for revised LTDS (what grid-related 'things' must be represented using the data structures on this worksheet) > Mandatory <list of data content that must be included in revised LTDS model, description of how it must be expressed) Allowed <list of alternate content that could be included or alternate ways in which it could be expressed) | [6 empty] | Summary of high-level differences - for the type of data on this worksheet - between existing LTDS and revised LTDS | Summary of existing LTDS requirements | Summary of proposed GC0139 requirements
Unsatisfied requirements | [9 empty] | list of identified requirements whose satisfaction strategy, in the revised CIM-based LTDS, has not yet been determined
Name of class being documented
Name of parent class documented elsewhere for profile
| Name of parent class | name of attribute |  | <LTDS profile(s) in which class appears> | <1..1 or 0..1>
| Name of parent class | name of attribute not used in profile |  | none
| Name of class being documented Description of class from UML (base + LTDS extensions) |  |  | LTDS profiles in which class appears [1] [2] |  | <additional class-level constraints (those not able to be expressed in rdfs profile)> | <CGMES profile in which class appears[1], if it does> | <CIM standard profile(s) in which class appears[1], if it does> | <yes or no> |  | p <n> <requirement from LTDS FoS related to class>
| Name of class | name of attribute | description of attribute from UML (base + LTDS extensions) | <LTDS profile(s) in which class appears> | <1..1 or 0..1> | <additional attribute-level constraints (those not able to be expressed in rdfs profile)> | If attribute in CGMIES profile: <CGMES profile(s) in which class appears> <1..1 or 0..1> | If attribute in CIM standard profile: <CIM standard profile(s) in which class appears> <1..1 or 0..1> | <yes or no> | <comment> <unanswered question> | p <n> <requirement from LTDS FoS related to attribute>
| Name of class | name of attribute not used in profile | description of attribute from UML (base + LTDS extensions) | none |  |  | If attribute not in CGMES profile: none | If attribute not in CIM standard profile: none | <yes or no>
|  | NOTE: all attributes of the class defined in UML (base + LTDS extensions) are listed regardless of their usage in a given profile. Unused attributes have 'none' in the LTDS profile column and have cells with grey backgrounds. |  |  |  |  | NOTE: the entries in these columns are completely independent of each other and of LTDS in terms of whether a given attribute appears or not
[5 empty] | question to be addressed in LTDS definition work |  | LTDS doesn’t match exactly | LTDS doesn't match exactly | LTDS attribute not in information model
[1] | does not include classes that appear in profile only because they are 'pointed to' by an association
[2] | bolded profile is profile in which object mRID is established
cells copied from class above in worksheet
grey text means class is always abstract in LTDS profiles, black text means it can (but not must) be concrete in LTDS profiles
modeling finalized
model question still exists
profile update required

## EQ SC SSH - Building Block
Class | Parent Class or Class | Attribute | Description (CIM Notes) | LTDS Profile | LTDS UML Constraint | LTDS Additional Constraints | Change from CGMES 3.0 | In CGMES 3.0 profile | In 61970-452 Ed4 EQ, SC, OP or 61970-456 Ed3 SSH profiles | In CIM information model | Comments / Questions | Existing LTDS requirement | Proposed GC0139 requirement
Instance Requirements |  |  | General philosophies: - initial scope of grid model is from Subtransmission to the HV bus in Primary substations plus any HV circuits interconnecting Primary substations - every bus in grid model scope that can be individually de-energized is modeled - every PowerTransformerEnd and every ACLineSegment have a BaseVoltage - every meaningful object has a name - only equipment that is normally in service appears in LTDS 'as is' modeling - BaseVoltage should be modeled as necessary to reflect the various nominal voltages of a DNO's system Mandatory - name is required on all IdentifiedObjects - <future note regarding the use of the Equipment.aggregate attribute - will be useful for aggregate load, generation, storage> |  |  |  | Nature of LTDS purpose means that only equipment normally in service should be provided, which led to removing one attribute in the EQ profile. LTDS requirement for short circuit information caused one attribute to be made mandatory that was optional. |  |  |  | Extension to existing LTDS: - initial grid scope is equivalent - additional bus attribute required to support short circuit analysis - object name is now defined in one place and cross table/diagram name mapping errors eliminated | grid scope: 132kV networks (EHV in Scotland) to the lower voltage busbars of primary substations (including details of any interconnectors at lower voltages that are needed to assess the capability of the higher voltage networks) naming: multiple references to "need for nomenclature to align"
IdentifiedObject
| IdentifiedObject This is a root class to provide common identification for all classes needing identification and naming attributes. |  |  | EQ, SC, OP, SSH |  |  |  |  | EQ, SC, OP, SSH | yes
| IdentifiedObject | aliasName | The aliasName is free text human readable name of the object alternative to IdentifiedObject.name. It may be non unique and may not correlate to a naming hierarchy. The attribute aliasName is retained because of backwards compatibility between CIM releases. It is however recommended to replace aliasName with the Name class as aliasName is planned for retirement at a future time. | none |  |  |  |  | none | yes
| IdentifiedObject | description | The description is a free human readable text describing or naming the object. It may be non unique and may not correlate to a naming hierarchy. | EQ, SC, OP | 0..1 |  |  |  | EQ, SC, OP 0..1 | yes
| IdentifiedObject | mRID | Master resource identifier issued by a model authority. The mRID is unique within an exchange context. Global uniqueness is easily achieved by using a UUID, as specified in IETF RFC 4122, for the mRID. The use of UUID is strongly recommended. For CIMXML data files in RDF syntax conforming to IEC 61970-552, the mRID is mapped to rdf:ID or rdf:about attributes that identify CIM object elements. | EQ, SC, OP, SSH | 1..1 |  |  |  | EQ, SC, OP, SSH 1..1 | yes
| IdentifiedObject | name | The name is any free human readable and possibly non unique text naming the object. | EQ, SC, OP | 1..1 |  |  |  | EQ, OP 1..1 | yes |  | multiple references to "need for nomenclature to align"
Equipment
IdentifiedObject
| IdentifiedObject | aliasName |  | none | 0
| IdentifiedObject | description |  | EQ, SC, OP | 0..1
| IdentifiedObject | mRID |  | EQ, SC, OP, SSH | 1..1
| IdentifiedObject | name |  | EQ, SC, OP | 1..1
| PowerSystemResource A power system resource (PSR) can be an item of equipment such as a switch, an equipment container containing many individual items of equipment such as a substation, or an organisational entity such as sub-control area. Power system resources can have measurements associated. |  |  | EQ, SC, OP, SSH |  |  |  |  | EQ, SC, OP, SSH | yes
| Equipment The parts of a power system that are physical devices, electronic or mechanical. |  |  | EQ, SC, SSH |  |  |  |  | EQ, SC, SSH | yes
| Equipment | aggregate | The aggregate flag provides an alternative way of representing an aggregated (equivalent) element. It is applicable in cases when the dedicated classes for equivalent equipment do not have all of the attributes necessary to represent the required level of detail. In case the flag is set to “true” the single instance of equipment represents multiple pieces of equipment that have been modelled together as an aggregate equivalent obtained by a network reduction procedure. Examples would be power transformers or synchronous machines operating in parallel modelled as a single aggregate power transformer or aggregate synchronous machine. The attribute is not used for EquivalentBranch, EquivalentShunt and EquivalentInjection. | EQ | 0..1 | if present shall be =true |  |  | EQ 0..1 | yes | Pat: This attribute will be considered when we get to load/generation modeling | maybe: p 11 "4 Generation may be aggregated by connection voltage and fuel type for any one particular substation" p 13 "3 Generation may be aggregated by connection voltage" p 15 "APPENDIX 1 – PROCESS FOR ASSESSING TREATMENT OF CUSTOMER SPECIFIC INFORMATION"
| Equipment | inService | Specifies the availability of the equipment. True means the equipment is available for topology processing, which determines if the equipment is energized or not. False means that the equipment is treated by network applications as if it is not in the model. | SSH | 0..1 | required (and =false) if equipment not in service, else no attribute |  |  | SSH 1..1 | yes
| Equipment | networkAnalysisEnabled | The equipment is enabled to participate in network analysis. If unspecified, the value is assumed to be true. | none |  |  |  |  | none | yes
| Equipment | normallyInService | Specifies the availability of the equipment under normal operating conditions. True means the equipment is available for topology processing, which determines if the equipment is energized or not. False means that the equipment is treated by network applications as if it is not in the model. | none |  |  | realized by profile change (removed attribute) | EQ 0..1 | EQ 0..1 | yes | Pat: if it's not normally in service, it shouldn't be published in the LTDS. Chavdar: we need to discuss if they really need this as in service info will come from SSH. I do not think they will run power flow on EQ only as they will not be able to do this anyway
ConductingEquipment
IdentifiedObject
| IdentifiedObject | aliasName |  | none | 0
| IdentifiedObject | description |  | EQ, SC, OP | 0..1
| IdentifiedObject | mRID |  | EQ, SC, OP, SSH | 1..1
| IdentifiedObject | name |  | EQ, SC, OP | 1..1
PowerSystemResource
Equipment
| Equipment | aggregate |  | EQ | 0..1
| Equipment | inService |  | SSH | 0..1
| Equipment | networkAnalysisEnabled |  | none | 0
| Equipment | normallyInService |  | none | 0
| ConductingEquipment The parts of the AC power system that are designed to carry current or that are conductively connected through terminals. |  |  | EQ, SC, SSH |  |  |  |  | EQ, SC, SSH | yes
Terminal
IdentifiedObject
| IdentifiedObject | aliasName |  | none | 0
| IdentifiedObject | description |  | EQ, SC, OP | 0..1
AUTO | IdentifiedObject | mRID |  | EQ, SC, OP, SSH | 1..1
AUTO | IdentifiedObject | name |  | EQ, SC, OP | 1..1
| ACDCTerminal An electrical connection point (AC or DC) to a piece of conducting equipment. Terminals are connected at physical connection points called connectivity nodes. |  |  | EQ |  |  |  |  | EQ | yes
| ACDCTerminal | connected | The connected status is related to a bus-branch model and the topological node to terminal relation. True implies the terminal is connected to the related topological node and false implies it is not. In a bus-branch model, the connected status is used to tell if equipment is disconnected without having to change the connectivity described by the topological node to terminal relation. A valid case is that conducting equipment can be connected in one end and open in the other. In particular for an AC line segment, where the reactive line charging can be significant, this is a relevant case. | SSH |  |  |  |  | SSH 1..1 | yes
AUTO | ACDCTerminal | sequenceNumber | The orientation of the terminal connections for a multiple terminal conducting equipment. The sequence numbering starts with 1 and additional terminals should follow in increasing order. The first terminal is the "starting point" for a two terminal branch. | EQ | 1..1 | sequenceNumbers of Terminals associated with a ConductingEquipment shall be unique, shall start with 1 and shall increment by one across Terminals |  |  | EQ 1..1 | yes
AUTO | Terminal An AC electrical connection point to a piece of conducting equipment. Terminals are connected at physical connection points called connectivity nodes. |  |  | EQ |  | the following types of ConductingEquipment (and their children) shall have 1 Terminal: - EnergyConnection - Connector the following shall have 2 Terminals: - ACLineSegment - Switch PowerTransformer shall have at least 2 Terminals |  |  | EQ | yes
| Terminal | phases | Represents the normal network phasing condition. If the attribute is missing, three phases (ABC) shall be assumed, except for terminals of grounding classes (specializations of EarthFaultCompensator, GroundDisconnector, and Ground) which will be assumed to be N. Therefore, phase code ABCN is explicitly declared when needed, e.g. for star point grounding equipment. The phase code on terminals connecting the same ConnectivityNode or TopologicalNode as well as for equipment between two terminals shall be consistent. | EQ | 0..1 | Add guidance related to use - only used when Terminal is associated with ???? |  |  | EQ 0..1 | yes | Pat: what are the constraints on this?
ConnectivityNode
IdentifiedObject
| IdentifiedObject | aliasName |  | none | 0
| IdentifiedObject | description |  | EQ, SC, OP | 0..1
AUTO | IdentifiedObject | mRID |  | EQ, SC, OP, SSH | 1..1
AUTO | IdentifiedObject | name |  | EQ, SC, OP | 1..1
AUTO | ConnectivityNode Connectivity nodes are points where terminals of AC conducting equipment are connected together with zero impedance. |  |  | EQ |  |  |  |  | EQ | yes
BaseVoltage
IdentifiedObject
| IdentifiedObject | aliasName |  | none | 0
| IdentifiedObject | description |  | EQ, SC, OP | 0..1
AUTO | IdentifiedObject | mRID |  | EQ, SC, OP, SSH | 1..1
YES | IdentifiedObject | name |  | EQ, SC, OP | 1..1
YES | BaseVoltage Defines a system base voltage which is referenced. |  |  | EQ |  | all ConductingEquipment (other than Power Transformer ) not directly or indirectly contained within a Substation shall have an association to BaseVoltage |  |  | EQ | yes
YES | BaseVoltage | nominalVoltage | The power system resource's base voltage. Shall be a positive value and not zero. | EQ | 1..1 |  |  |  | EQ 1..1 | yes |  | p 5 "General network characteristics including descriptions of: …. Operating voltages (target and bandwidth) for each voltage level of the distribution network" p 7 "TABLE 1 - CIRCUIT DATA …Operating Voltage" p 8 "TABLE 2 - TRANSFORMER DATA …Node 1 ..Voltage ..Node 2 ..Voltage" p 9 "TABLE 3 - LOAD INFORMATION …Voltage Level" p 10 "TABLE 4 - FAULT LEVEL INFORMATION …Voltage Level" | Schedule 5 - 2W TRANSFORMERS, 3W TRANSFORMERS worksheets … kV on nodes associated to windings
Connector>BusbarSection | [10 empty] | Please add BusbarSection to CP_BuildingBlock diagram
IdentifiedObject
| IdentifiedObject | aliasName |  | none | 0
| IdentifiedObject | description |  | EQ, SC, OP | 0..1
AUTO | IdentifiedObject | mRID |  | EQ, SC, OP, SSH | 1..1
YES | IdentifiedObject | name |  | EQ, SC, OP | 1..1
PowerSystemResource
Equipment
| Equipment | aggregate |  | EQ | 0..1
| Equipment | inService |  | SSH | 0..1
| Equipment | networkAnalysisEnabled |  | none | 0
| Equipment | normallyInService |  | none | 0
ConductingEquipment
| Connector A conductor, or group of conductors, with negligible impedance, that serve to connect other conducting equipment within a single substation and are modelled with a single logical terminal. |  |  | EQ |  |  |  |  | EQ, SC | yes
| BusbarSection A conductor, or group of conductors, with negligible impedance, that serve to connect other conducting equipment within a single substation. Voltage measurements are typically obtained from voltage transformers that are connected to busbar sections. A bus bar section may have many physical terminals but for analysis is modelled with exactly one logical terminal. |  |  | EQ, SC |  |  |  |  | EQ, SC | yes |  | p 7 "TABLE 1 - CIRCUIT DATA …S/S or Busbar Name" p 8 "TABLE 2 - TRANSFORMER DATA …S/S or Busbar Name" p 9 "TABLE 3 - LOAD INFORMATION …S/S or Busbar Name" p 10 "TABLE 4 - FAULT LEVEL INFORMATION …S/S or Busbar Name"
| BusbarSection | ipMax | Maximum allowable peak short-circuit current of busbar (Ipmax in IEC 60909-0). Mechanical limit of the busbar in the substation itself. Used for short circuit data exchange according to IEC 60909. | SC | 1..1 |  | realized by cardinality change (from optional to mandatory) | EQ 0..1 | EQ 0..1 | yes | Pat: this should be required, right?

## EQ SSH - Switch
Class | Parent Class or Class | Attribute | Description (CIM Notes) | LTDS Profile | LTDS UML Constraint | LTDS Additional Constraints | Change from CGMES 3.0 | In CGMES 3.0 profile | In 61970-452 Ed4 EQ, SC, OP or 61970-456 Ed3 SSH profiles | In CIM information model | Comments / Questions | Existing LTDS requirement | Proposed GC0139 requirement
Instance Requirements |  |  | General philosophy: Switch devices are modeled such that the system topology can be modified as required for user studies Mandatory For all grid scope: - line breakers modeled using Breaker - breakers associated with transformers modeled using Breaker (sufficient for outaging transformer) - bus coupling breakers modeled using Breaker - bus coupling switches (not associated with Breaker) modeled using Disconnector - breakers suffient to outage generators modeled using Breaker Allowed - Use of any CIM class more explicit than the one required - Modeling of additional switch devices beyond the required |  |  |  | LTDS requirement for support of fault infeed calculations required an attribute to be made manadatory instead of optional in the EQ profile and an attribute to be added to the SC profile. |  |  |  | Significant expansion of existing LTDS: - from no data on individual switches to modeling individual switches with several attributes | p 6 "Normal open points shall be clearly indicated on all schematic diagrams" | Grid scope is different between proposed LTDS and GC0139, but LTDS switch instance philosophy is intended to mirror GC0139
Unsatisfied requirements
Switch
IdentifiedObject
| IdentifiedObject | aliasName
| IdentifiedObject | description
| IdentifiedObject | mRID
| IdentifiedObject | name
PowerSystemResource
Equipment
| Equipment | aggregate
| Equipment | inService
| Equipment | networkAnalysisEnabled
| Equipment | normallyInService
ConductingEquipment
| Switch A generic device designed to close, or open, or both, one or more electric circuits. All switches are two terminal devices including grounding switches. The ACDCTerminal.connected at the two sides of the switch shall not be considered for assessing switch connectivity, i.e. only Switch.open, .normalOpen and .locked are relevant. |  |  | EQ, SSH |  |  |  |  | EQ, SSH | yes
| Switch | locked | If true, the switch is locked. The resulting switch state is a combination of locked and Switch.open attributes as follows: locked=true and Switch.open=true. The resulting state is open and locked; locked=false and Switch.open=true. The resulting state is open; locked=false and Switch.open=false. The resulting state is closed. | [5 empty] | SSH 1..1 | yes
| Switch | normalOpen | The attribute is used in cases when no Measurement for the status value is present. If the Switch has a status measurement the Discrete.normalValue is expected to match with the Switch.normalOpen. | EQ | 1..1 |  |  |  | EQ 1..1 | yes
| Switch | open | The attribute tells if the switch is considered open when used as input to topology processing. | [5 empty] | SSH 1..1 | yes | why isn't .open only needed if =true?
| Switch | ratedCurrent | The maximum continuous current carrying capacity in amps governed by the device material and construction. The attribute shall be a positive value. | EQ | 1..1 |  | realized by cardinality change (from optional to mandatory) | EQ 0..1 | EQ 0..1 | yes
| Switch | retained | Branch is retained in the topological solution. The flow through retained switches will normally be calculated in power flow. | EQ | 1..1 | must be=true |  |  | EQ 1..1 | yes | MAY CHANGE raising issue with WG13 as to whether this should be SSH
Disconnector
IdentifiedObject
| IdentifiedObject | aliasName
| IdentifiedObject | description
AUTO | IdentifiedObject | mRID
YES | IdentifiedObject | name
PowerSystemResource
Equipment
| Equipment | aggregate
| Equipment | inService
| Equipment | networkAnalysisEnabled
| Equipment | normallyInService
ConductingEquipment
Switch
| Switch | locked |  | 0 | 0
YES | Switch | normalOpen |  | EQ | 1..1
| Switch | open |  | 0 | 0
YES | Switch | ratedCurrent |  | EQ | 1..1
| Switch | retained |  | EQ | 1..1
YES | Disconnector A manually operated or motor operated mechanical switching device used for changing the connections in a circuit, or for isolating a circuit or equipment from a source of power. It is required to open or close circuits when negligible current is broken or made. |  |  | EQ, SSH |  |  |  |  | EQ, SSH | yes
Fuse
IdentifiedObject
| IdentifiedObject | aliasName
| IdentifiedObject | description
| IdentifiedObject | mRID
| IdentifiedObject | name
PowerSystemResource
Equipment
| Equipment | aggregate
| Equipment | inService
| Equipment | networkAnalysisEnabled
| Equipment | normallyInService
ConductingEquipment
Switch
| Switch | locked |  | 0 | 0
| Switch | normalOpen |  | EQ | 1..1
| Switch | open |  | 0 | 0
| Switch | ratedCurrent |  | EQ | 1..1
| Switch | retained |  | EQ | 1..1
| Fuse An overcurrent protective device with a circuit opening fusible part that is heated and severed by the passage of overcurrent through it. A fuse is considered a switching device because it breaks current. |  |  | EQ, SSH |  |  |  |  | EQ, SSH | yes
GroundDisconnector
IdentifiedObject
| IdentifiedObject | aliasName
| IdentifiedObject | description
| IdentifiedObject | mRID
| IdentifiedObject | name
PowerSystemResource
Equipment
| Equipment | aggregate
| Equipment | inService
| Equipment | networkAnalysisEnabled
| Equipment | normallyInService
ConductingEquipment
Switch
| Switch | locked |  | 0 | 0
| Switch | normalOpen |  | EQ | 1..1
| Switch | open |  | 0 | 0
| Switch | ratedCurrent |  | EQ | 1..1
| Switch | retained |  | EQ | 1..1
| GroundDisconnector A manually operated or motor operated mechanical switching device used for isolating a circuit or equipment from ground. |  |  | EQ, SSH |  |  |  |  | EQ, SSH | yes
Jumper
IdentifiedObject
| IdentifiedObject | aliasName
| IdentifiedObject | description
| IdentifiedObject | mRID
| IdentifiedObject | name
PowerSystemResource
Equipment
| Equipment | aggregate
| Equipment | inService
| Equipment | networkAnalysisEnabled
| Equipment | normallyInService
ConductingEquipment
Switch
| Switch | locked |  | 0 | 0
| Switch | normalOpen |  | EQ | 1..1
| Switch | open |  | 0 | 0
| Switch | ratedCurrent |  | EQ | 1..1
| Switch | retained |  | EQ | 1..1
| Jumper A short section of conductor with negligible impedance which can be manually removed and replaced if the circuit is de-energized. Note that zero-impedance branches can potentially be modelled by other equipment types. |  |  | EQ, SSH |  |  |  |  | EQ, SSH | yes
ProtectedSwitch
IdentifiedObject
| IdentifiedObject | aliasName
| IdentifiedObject | description
| IdentifiedObject | mRID
| IdentifiedObject | name
PowerSystemResource
Equipment
| Equipment | aggregate
| Equipment | inService
| Equipment | networkAnalysisEnabled
| Equipment | normallyInService
ConductingEquipment
Switch
| Switch | locked |  | 0 | 0
| Switch | normalOpen |  | EQ | 1..1
| Switch | open |  | 0 | 0
| Switch | ratedCurrent |  | EQ | 1..1
| Switch | retained |  | EQ | 1..1
| ProtectedSwitch A ProtectedSwitch is a switching device that can be operated by ProtectionEquipment. |  |  | EQ, SSH |  |  |  |  | EQ, SSH | yes
| ProtectedSwitch | breakingCapacity | The maximum fault current a breaking device can break safely under prescribed conditions of use. | SC | 1..1 |  | realized by profile change (added attribute) | none | none | yes
Breaker
IdentifiedObject
| IdentifiedObject | aliasName
| IdentifiedObject | description
AUTO | IdentifiedObject | mRID
YES | IdentifiedObject | name
PowerSystemResource
Equipment
| Equipment | aggregate
| Equipment | inService
| Equipment | networkAnalysisEnabled
| Equipment | normallyInService
ConductingEquipment
Switch
| Switch | locked |  | 0 | 0
YES | Switch | normalOpen |  | EQ | 1..1
| Switch | open |  | 0 | 0
YES | Switch | ratedCurrent |  | EQ | 1..1
| Switch | retained |  | EQ | 1..1
ProtectedSwitch
YES | ProtectedSwitch | breakingCapacity |  | SC | 1..1
YES | Breaker A mechanical switching device capable of making, carrying, and breaking currents under normal circuit conditions and also making, carrying for a specified time, and breaking currents under specified abnormal circuit conditions e.g. those of short circuit. |  |  | EQ, SC, SSH |  |  |  |  | EQ, SSH | yes
| Breaker | inTransitTime | The transition time from open to close. | none |  |  |  |  | none | yes
DisconnectingCircuitBreaker
IdentifiedObject
| IdentifiedObject | aliasName
| IdentifiedObject | description
| IdentifiedObject | mRID
| IdentifiedObject | name
PowerSystemResource
Equipment
| Equipment | aggregate
| Equipment | inService
| Equipment | networkAnalysisEnabled
| Equipment | normallyInService
ConductingEquipment
Switch
| Switch | locked |  | 0 | 0
| Switch | normalOpen |  | EQ | 1..1
| Switch | open |  | 0 | 0
| Switch | ratedCurrent |  | EQ | 1..1
| Switch | retained |  | EQ | 1..1
ProtectedSwitch
| ProtectedSwitch | breakingCapacity |  | SC | 1..1
Breaker
| Breaker | inTransitTime |  | none | 0
| DisconnectingCircuitBreaker A circuit breaking device including disconnecting function, eliminating the need for separate disconnectors. |  |  | EQ, SSH |  |  |  |  | EQ, SSH | yes
LoadBreakSwitch
IdentifiedObject
| IdentifiedObject | aliasName
| IdentifiedObject | description
| IdentifiedObject | mRID
| IdentifiedObject | name
PowerSystemResource
Equipment
| Equipment | aggregate
| Equipment | inService
| Equipment | networkAnalysisEnabled
| Equipment | normallyInService
ConductingEquipment
Switch
| Switch | locked |  | 0 | 0
| Switch | normalOpen |  | EQ | 1..1
| Switch | open |  | 0 | 0
| Switch | ratedCurrent |  | EQ | 1..1
| Switch | retained |  | EQ | 1..1
ProtectedSwitch
| ProtectedSwitch | breakingCapacity |  | SC | 1..1
| LoadBreakSwitch A mechanical switching device capable of making, carrying, and breaking currents under normal operating conditions. |  |  | EQ, SSH |  |  |  |  | EQ, SSH | yes

## EQ SC SSH - ACLineSegment
Class | Parent Class or Class | Attribute | Description (CIM Notes) | LTDS Profile | LTDS UML Constraint | LTDS Additional Constraints | Change from CGMES 3.0 | In CGMES 3.0 profile | In 61970-452 Ed4 EQ, SC, OP or 61970-456 Ed3 SSH profiles | In CIM information model | Comments / Questions | Existing LTDS requirement | Proposed GC0139 requirement
Instance Requirements |  |  | General philosophy: Every DNO-operated circuit above HV voltage is modeled; in addition, every HV circuit which interconnects Primary substations is modeled Mandatory For all grid scope: - at least one ACLineSegment is modeled for each circuit and it has both positive- and zero-sequence impedance values which are expressed either for the whole circuit or as a per length value - sections of 132 kV circuits in sufficiently close proximity to have mutual coupling effects are modeled individually and impedance values are provided reflecting mutual effects Allowed - Use of multiple ACLineSegments to model a circuit, especially if the modeling reflects sections with differing impedances |  |  |  | not yet settled |  |  |  | Expansion of existing LTDS: - zero-sequence impedance values added to support short circuit analysis - modeling of mutuals added Reduction of existing LTDS: - line length required only if impedances are expressed in per length [Information on line ratings is OperationalLimitSets worrksheet] | Scope is "132kV networks (EHV in Scotland) to the lower voltage busbars of primary substations but includes details of any interconnectors at lower voltages that are needed to assess the capability of the higher voltage networks." Circuit values include positive sequence impedance and a single rating. | Grid scope is different between proposed LTDS and GC0139. GC0139 circuit values include positive sequence impedance and 4 seasonal ratings. GC0139 calls for modeling of mutuals.
Unsatisfied requirements |  |  | Should we allow per length impedance descriptions?
Conductor>ACLineSegment
IdentifiedObject
| IdentifiedObject | aliasName
| IdentifiedObject | description
AUTO | IdentifiedObject | mRID
YES | IdentifiedObject | name
PowerSystemResource
Equipment
| Equipment | aggregate
| Equipment | inService
| Equipment | networkAnalysisEnabled
| Equipment | normallyInService
ConductingEquipment
| Conductor Combination of conducting material with consistent electrical characteristics, building a single electrical system, used to carry current between points in the power system. |  |  | EQ |  |  |  |  | EQ, SC | yes
YES | Conductor | length | Segment length for calculating line segment capabilities. | EQ | 0..1 | required if ACLineSegment has associated PerLengthSequenceImpedance or a PerLengthPhaseImpedance |  | EQ 0..1 | EQ 0..1 | yes |  | p 7 "TABLE 1 - CIRCUIT DATA …Circuit Length" p 7 "6 Details of circuit length should be included in this table or clearly marked on schematic diagrams unless this information can be estimated by the user from the geographic plans within the Statement."
| ACLineSegment A line segment is a conductor or combination of conductors, with consistent electrical characteristics along its length, building a single electrical system that carries alternating current between two points in the power system. The BaseVoltage at the two ends of a line segment shall have the same BaseVoltage.nominalVoltage. However, boundary lines may have slightly different BaseVoltage.nominalVoltages and variation is allowed. Larger voltage difference in general requires use of an equivalent branch. Line segment impedances can be either directly described in electrical terms or physical line detail can be provided from which impedances can be calculated. Directly described impedances For symmetrical, transposed three phase line segments, it is sufficient to use attributes of the line segment, which describe impedances and admittances for the entire length of the line segment. Additionally line segment impedances can be computed by using line segment length and associated per length impedances. Unbalanced modeling of impedances is supported by the phase-to-phase per length impedance matrix (PerLengthPhaseImpedance), with or without support from line segment phases. (The phase-to-phase per length impedance matrix, with fromPhase and toPhase attributes populated, is sufficient to fully describe impedances without line segment phases.) Either way, the length of the line segment is used in the computation of total impedance values for the line segment. Line detail characteristics There are three approaches to providing line detail and all used WireAssembly to supply line positions: Option 1 - WireAssembly supplies only line positions. ACLineSegmentPhase points to wire type and bundle type and supplies the position to phase mapping. Option 2 - WireAssembly supplies line position and, for each position, also supplies wire type and bundle type. ACLineSegmentPhase supplies the position to phase mapping. Option 3 - WireAssembly supplies line position, for each position, also supplies wire type and bundle type and phase. ACLineSegmentPhase is not needed. |  |  | EQ, SC |  |  |  |  | EQ, SC | yes
YES | ACLineSegment | b0ch | Zero sequence shunt (charging) susceptance, uniformly distributed, of the entire line section. | SC | 0..1 | required if ACLineSegment does not have a PerLengthSequenceImpedance or a PerLengthPhaseImpedance |  |  | SC 1..1 | yes | will be required if per length impedances not allowed |  | Schedule 5 - LINES worksheet …B1 in MVAr
YES | ACLineSegment | bch | Positive sequence shunt (charging) susceptance, uniformly distributed, of the entire line section. This value represents the full charging over the full length of the line. | EQ | 0..1 | required if ACLineSegment does not have a PerLengthSequenceImpedance or a PerLengthPhaseImpedance |  |  | EQ 1..1 | yes | will be required if per length impedances not allowed | p 6 "The main categories of this information shall be listed in the Statement and include: ...Circuits – Susceptance data for voltage levels other than 132kV" p 7 "TABLE 1 - CIRCUIT DATA …Susceptance …B" p 7 "4 Susceptance information should be included for 132kV networks and available on request at other voltage levels." | Schedule 5 - LINES worksheet …B1 in MVAr
YES | ACLineSegment | g0ch | Zero sequence shunt (charging) conductance, uniformly distributed, of the entire line section. | SC | 0..1 | required if ACLineSegment does not have a PerLengthSequenceImpedance or a PerLengthPhaseImpedance |  |  | SC 1..1 | yes | will be required if per length impedances not allowed
YES | ACLineSegment | gch | Positive sequence shunt (charging) conductance, uniformly distributed, of the entire line section. | EQ | 0..1 | required if ACLineSegment does not have a PerLengthSequenceImpedance or a PerLengthPhaseImpedance |  | EQ 0..1 | EQ 0..1 | yes | will be required if per length impedances not allowed
YES | ACLineSegment | r | Positive sequence series resistance of the entire line section. | EQ | 0..1 | required if ACLineSegment does not have a PerLengthSequenceImpedance or a PerLengthPhaseImpedance |  |  | EQ 1..1 | yes | will be required if per length impedances not allowed | p 7 "TABLE 1 - CIRCUIT DATA …Positive Sequence Impedance …R" | Schedule 5 - LINES worksheet ...R1 % on 100MVA base
YES | ACLineSegment | r0 | Zero sequence series resistance of the entire line section. | SC | 0..1 | required if ACLineSegment does not have a PerLengthSequenceImpedance or a PerLengthPhaseImpedance |  |  | SC 1..1 | yes | will be required if per length impedances not allowed | p 6 "The main categories of this information shall be listed in the Statement and include: ...Circuits - Zero sequence impedance data" | Schedule 5 - LINES worksheet ...R0 % on 100MVA base
| ACLineSegment | shortCircuitEndTemperature | Maximum permitted temperature at the end of SC for the calculation of minimum short-circuit currents. Used for short circuit data exchange according to IEC 60909. | SC |  |  |  |  | SC 1..1 | yes | Note that it does not show up in the ENTSO-E note Mohammed sent.
YES | ACLineSegment | x | Positive sequence series reactance of the entire line section. | EQ | 0..1 | required if ACLineSegment does not have a PerLengthSequenceImpedance or a PerLengthPhaseImpedance |  |  | EQ 1..1 | yes | will be required if per length impedances not allowed | p 7 "TABLE 1 - CIRCUIT DATA …Positive Sequence Impedance …X" | Schedule 5 - LINES worksheet ...X1 % on 100MVA base
YES | ACLineSegment | x0 | Zero sequence series reactance of the entire line section. | SC | 0..1 | required if ACLineSegment does not have a PerLengthSequenceImpedance or a PerLengthPhaseImpedance |  |  | SC 1..1 | yes | will be required if per length impedances not allowed | p 6 "The main categories of this information shall be listed in the Statement and include: ...Circuits - Zero sequence impedance data" | Schedule 5 - LINES worksheet ...X0 % on 100MVA base
PerLengthLineParameter>PerLengthImpedance
IdentifiedObject
| IdentifiedObject | aliasName
| IdentifiedObject | description
| IdentifiedObject | mRID
| IdentifiedObject | name
| PerLengthLineParameter Common type for per-length electrical catalogues describing line parameters. |  |  | EQ, SC |  |  |  | none | none
| PerLengthImpedance Common type for per-length impedance electrical catalogues. |  |  | EQ, SC |  |  |  | none | none
PerLengthSequenceImpedance
IdentifiedObject
| IdentifiedObject | aliasName
| IdentifiedObject | description
| IdentifiedObject | mRID
| IdentifiedObject | name
PerLengthLineParameter Common type for per-length impedance electrical catalogues.
PerLengthImpedance
| PerLengthSequenceImpedance Sequence impedance and admittance parameters per unit length, for transposed lines of 1, 2, or 3 phases. For 1-phase lines, define x=x0=xself. For 2-phase lines, define x=xs-xm and x0=xs+xm. |  |  | EQ, SC |  | required if ACLineSegment does not have values populated for all impedance attributes and does not have a PerLengthPhaseImpedance |  | none | none | yes | Should we allow per length impedance descriptions?
| PerLengthSequenceImpedance | b0ch | Zero sequence shunt (charging) susceptance, per unit of length. | SC | 1..1 |  |  | none | none | yes
| PerLengthSequenceImpedance | bch | Positive sequence shunt (charging) susceptance, per unit of length. | EQ | 1..1 |  |  | none | none | yes
| PerLengthSequenceImpedance | g0ch | Zero sequence shunt (charging) conductance, per unit of length. | SC | 1..1 |  |  | none | none | yes
| PerLengthSequenceImpedance | gch | Positive sequence shunt (charging) conductance, per unit of length. | EQ | 1..1 |  |  | none | none | yes
| PerLengthSequenceImpedance | r | Positive sequence series resistance, per unit of length. | EQ | 1..1 |  |  | none | none | yes
| PerLengthSequenceImpedance | r0 | Zero sequence series resistance, per unit of length. | SC | 1..1 |  |  | none | none | yes
| PerLengthSequenceImpedance | x | Positive sequence series reactance, per unit of length. | EQ | 1..1 |  |  | none | none | yes
| PerLengthSequenceImpedance | x0 | Zero sequence series reactance, per unit of length. | SC | 1..1 |  |  | none | none | yes
MutualCoupling | [10 empty] | Chavdar: We have all the pink already in 452 and CGMES Pat: Got it. Can we add MutualCoupling to the CP_ACLineSegment diagram, please?
IdentifiedObject
| IdentifiedObject | aliasName
| IdentifiedObject | description
| IdentifiedObject | mRID
| IdentifiedObject | name
| MutualCoupling This class represents the zero sequence line mutual coupling. |  |  | SC |  |  |  |  | SC | yes
| MutualCoupling | b0ch | Zero sequence mutual coupling shunt (charging) susceptance, uniformly distributed, of the entire line section. | SC | 1..1 |  |  |  | SC 1..1 | yes
| MutualCoupling | distance11 | Distance to the start of the coupled region from the first line's terminal having sequence number equal to 1. | SC | 1..1 |  |  |  | SC 1..1 | yes | Pat: can we please eliminate these attributes and just tell folks they need to model individual ACLineSegments that either are 100% parallel or are not parallel? Chavdar: I think if we remove them the model would not work. This will need form further discussion
| MutualCoupling | distance12 | Distance to the end of the coupled region from the first line's terminal with sequence number equal to 1. | SC | 1..1 |  |  |  | SC 1..1 | yes | ditto
| MutualCoupling | distance21 | Distance to the start of coupled region from the second line's terminal with sequence number equal to 1. | SC | 1..1 |  |  |  | SC 1..1 | yes | ditto
| MutualCoupling | distance22 | Distance to the end of coupled region from the second line's terminal with sequence number equal to 1. | SC | 1..1 |  |  |  | SC 1..1 | yes | ditto
| MutualCoupling | g0ch | Zero sequence mutual coupling shunt (charging) conductance, uniformly distributed, of the entire line section. | SC | 1..1 |  |  |  | SC 1..1 | yes
| MutualCoupling | r0 | Zero sequence branch-to-branch mutual impedance coupling, resistance. | SC | 1..1 |  |  |  | SC 1..1 | yes
| MutualCoupling | x0 | Zero sequence branch-to-branch mutual impedance coupling, reactance. | SC | 1..1 |  |  |  | SC 1..1 | yes

## EQ SC SSH -PowerTransformer
Class | Parent Class or Class | Attribute | Description (CIM Notes) | LTDS Profile | LTDS UML Constraint | LTDS Additional Constraints | Change from CGMES 3.0 | In CGMES 3.0 profile | In 61970-452 Ed4 EQ, SC, OP or 61970-456 Ed3 SSH profiles | In CIM information model | Comments / Questions | Existing LTDS requirement | Proposed GC0139 requirement
Instance Requirements |  |  | General philosophy: Every transformer in a Subtransmission, EHV or Primary substation is modeled Mandatory - complete modeling of every transformer, including impedance and short circuit information, terminal voltage phase angle displacement, vector group and grounding information Allowed - |  |  |  | Support for fault level studies has led to inclusion of a number of existing attributes in the SC profile. More detailed LTDS requirements related to modeling of transformer winding information resulted in a new TransformerEnd attribute replacing an existing one in the information model and SC profile and an attribute being made mandatory in the EQ profile. Also the addition of an enumeration class. Use of OperationalLimitSets for on transformer windings eliminated need for winding rating and resulted in the removal of an attribute from PowerTransformerEnd in the EQ profile. |  |  |  | Significant expansion of existing LTDS: New information - additional zero-sequence impedance data - new short circuit information - new resistive and reactive parts of neutral impedance (GC0139 has them) Revised LTDS has different forms of expression for rating, vector group and grounding, but content is roughly the same as existing | Any transformer whose high voltage is 132kV (EHV in Scotland) or less, down to and including transformers in primary substations
Unsatisfied requirements |  |  | Discuss the mechanics by which the 3-winding table entries from Eastern Power Networks (UKPN) would be used to populate PowerTransformerEnd impedances (without using TransformerMeshImpedance) | [9 empty] | Schedule 5 - 3W TRANSFORMERS worksheet … (pu Minimum V) … (pu Maximum V) Schedule 5 - 2W TRANSFORMERS worksheet … (pu Minimum V) … (pu Maximum V)
PowerTransformer
IdentifiedObject
| IdentifiedObject | aliasName
| IdentifiedObject | description
AUTO | IdentifiedObject | mRID
YES | IdentifiedObject | name
PowerSystemResource
Equipment
| Equipment | aggregate
| Equipment | inService
| Equipment | networkAnalysisEnabled
| Equipment | normallyInService
ConductingEquipment
| PowerTransformer An electrical device consisting of two or more coupled windings, with or without a magnetic core, for introducing mutual coupling between electric circuits. Transformers can be used to control voltage and phase shift (active power flow). A power transformer may be composed of separate transformer tanks that need not be identical. A power transformer can be modelled with or without tanks and is intended for use in both balanced and unbalanced representations. A power transformer typically has two terminals, but may have one (grounding), three or more terminals. The inherited association ConductingEquipment.BaseVoltage should not be used. The association from TransformerEnd to BaseVoltage should be used instead. |  |  | EQ, SC | PowerTransformer shall not have an association to BaseVoltage |  |  |  | EQ, SC | yes
YES | PowerTransformer | beforeShCircuitHighestOperationCurrent | The highest operating current (Ib in IEC 60909-0) before short circuit (depends on network configuration and relevant reliability philosophy). It is used for calculation of the impedance correction factor KT defined in IEC 60909-0. | SC | 1..1 |  | realized by cardinality change (from optional to mandatory) | SC 0..1 | SC 0..1 | yes
YES | PowerTransformer | beforeShCircuitHighestOperationVoltage | The highest operating voltage (Ub in IEC 60909-0) before short circuit. It is used for calculation of the impedance correction factor KT defined in IEC 60909-0. This is worst case voltage on the low side winding (3.7.1 of IEC 60909:2001). Used to define operating conditions. | SC | 1..1 |  | realized by cardinality change (from optional to mandatory) | SC 0..1 | SC 0..1 | yes
YES | PowerTransformer | beforeShortCircuitAnglePf | The angle of power factor before short circuit (phib in IEC 60909-0). It is used for calculation of the impedance correction factor KT defined in IEC 60909-0. This is the worst case power factor. Used to define operating conditions. | SC | 1..1 |  | realized by cardinality change (from optional to mandatory) | SC 0..1 | SC 0..1 | yes
YES | PowerTransformer | highSideMinOperatingU | The minimum operating voltage (uQmin in IEC 60909-0) at the high voltage side (Q side) of the unit transformer of the power station unit. A value well established from long-term operating experience of the system. It is used for calculation of the impedance correction factor KG defined in IEC 60909-0. | SC | 1..1 |  | realized by cardinality change (from optional to mandatory) | SC 0..1 | SC 0..1 | yes
YES | PowerTransformer | isPartOfGeneratorUnit | Indicates whether the machine is part of a power station unit. Used for short circuit data exchange according to IEC 60909. It has an impact on how the correction factors are calculated for transformers, since the transformer is not necessarily part of a synchronous machine and generating unit. It is not always possible to derive this information from the model. This is why the attribute is necessary. | SC | 1..1 |  | realized by cardinality change (from optional to mandatory) | SC 0..1 | SC 0..1 | yes
YES | PowerTransformer | operationalValuesConsidered | It is used to define if the data (other attributes related to short circuit data exchange) defines long term operational conditions or not. Used for short circuit data exchange according to IEC 60909. | SC | 1..1 |  | realized by cardinality change (from optional to mandatory) | SC 0..1 | SC 0..1 | yes
| PowerTransformer | vectorGroup | Vector group of the transformer for protective relaying, e.g., Dyn1. For unbalanced transformers, this may not be simply determined from the constituent winding connections and phase angle displacements. The vectorGroup string consists of the following components in the order listed: high voltage winding connection, mid voltage winding connection (for three winding transformers), phase displacement clock number from 0 to 11, low voltage winding connection phase displacement clock number from 0 to 11. The winding connections are D (delta), Y (wye), YN (wye with neutral), Z (zigzag), ZN (zigzag with neutral), A (auto transformer). Upper case means the high voltage, lower case mid or low. The high voltage winding always has clock position 0 and is not included in the vector group string. Some examples: YNy0 (two winding wye to wye with no phase displacement), YNd11 (two winding wye to delta with 330 degrees phase displacement), YNyn0d5 (three winding transformer wye with neutral high voltage, wye with neutral mid voltage and no phase displacement, delta low voltage with 150 degrees displacement). Phase displacement is defined as the angular difference between the phasors representing the voltages between the neutral point (real or imaginary) and the corresponding terminals of two windings, a positive sequence voltage system being applied to the high-voltage terminals, following each other in alphabetical sequence if they are lettered, or in numerical sequence if they are numbered: the phasors are assumed to rotate in a counter-clockwise sense. | none |  |  |  | none | none | yes
TransformerEnd>PowerTransformerEnd
IdentifiedObject
| IdentifiedObject | aliasName
| IdentifiedObject | description
AUTO | IdentifiedObject | mRID
YES | IdentifiedObject | name
| TransformerEnd A conducting connection point of a power transformer. It corresponds to a physical transformer winding terminal. In earlier CIM versions, the TransformerWinding class served a similar purpose, but this class is more flexible because it associates to terminal but is not a specialization of ConductingEquipment. |  |  | EQ, SC |  |  |  |  | EQ, SC | yes
| TransformerEnd | bmagSat | Core shunt magnetizing susceptance in the saturation region. | none |  |  |  |  | none | yes
YES | TransformerEnd | endNumber | Number for this transformer end, corresponding to the end's order in the power transformer vector group or phase angle clock number. Highest voltage winding should be 1. Each end within a power transformer should have a unique subsequent end number. Note the transformer end number need not match the terminal sequence number. | EQ | 1..1 |  |  |  | EQ 1..1 | yes
| TransformerEnd | grounded | (for Yn and Zn connections) True if the neutral is grounded. | none |  |  | realized by profile change (removed attribute) | SC 1..1 | SC 1..1 | yes | Boolean is insufficient for LTDS, replaced by new .earthingMethod attribute
| TransformerEnd | magBaseU | The reference voltage at which the magnetizing saturation measurements were made. | none |  |  |  |  | none | yes
| TransformerEnd | magSatFlux | Core magnetizing saturation curve knee flux level. | none |  |  |  |  | none | yes
OPTIONAL | TransformerEnd | rground | (for Yn and Zn connections) Resistance part of neutral impedance where 'grounded' is true. | SC | 0..1 | required if .earthingMethod=Solid Grounding or Resistance Grounding, else no attribute |  | SC 0..1 | SC 0..1 | yes | Pat: what should the constraints be? |  | Schedule 5 - 2W TRANSFORMERS worksheet …HV R grounding in ohms …LV R grounding in ohms Schedule 5 - 3W TRANSFORMERS worksheet …HV R grounding in ohms …MV R grounding in ohms …LV R grounding in ohms
OPTIONAL | TransformerEnd | xground | (for Yn and Zn connections) Reactive part of neutral impedance where 'grounded' is true. | SC | 0..1 | required if .earthingMethod=Solid Grounding or Reactance Grounding, else no attribute |  | SC 0..1 | SC 0..1 | yes | Pat: what should the constraints be? |  | Schedule 5 - 2W TRANSFORMERS worksheet …HV X grounding in ohms …LV X grounding in ohms Schedule 5 - 3W TRANSFORMERS worksheet …HV X grounding in ohms …MV X grounding in ohms …LV X grounding in ohms
YES | TransformerEnd | earthingMethod | Type of grounding. | SC | 1..1 | there is probably a correlation between PowerTransformerEnd.connectionKind and TransformerEnd.earthingMethod that should be enforced | realized by extension and profile change (added attribute) | none | none | no |  | p 5 "Methods of earthing used on different voltage levels or regions" p 6 "The main categories of this information shall be listed in the Statement and include: ...Transformers – Earthing details (including identification of hot substation sites)" p 8 "TABLE 2 - TRANSFORMER DATA …Method of Earthing" | Schedule 5 - 2W TRANSFORMERS worksheet …HV grounding type …LV grounding type Schedule 5 - 3W TRANSFORMERS worksheet …HV grounding type …MV grounding type …LV grounding type
| PowerTransformerEnd A PowerTransformerEnd is associated with each Terminal of a PowerTransformer. The impedance values r, r0, x, and x0 of a PowerTransformerEnd represents a star equivalent as follows. 1) for a two Terminal PowerTransformer the high voltage (TransformerEnd.endNumber=1) PowerTransformerEnd has non zero values on r, r0, x, and x0 while the low voltage (TransformerEnd.endNumber=2) PowerTransformerEnd has zero values for r, r0, x, and x0. Parameters are always provided, even if the PowerTransformerEnds have the same rated voltage. In this case, the parameters are provided at the PowerTransformerEnd which has TransformerEnd.endNumber equal to 1. 2) for a three Terminal PowerTransformer the three PowerTransformerEnds represent a star equivalent with each leg in the star represented by r, r0, x, and x0 values. 3) For a three Terminal transformer each PowerTransformerEnd shall have g, g0, b and b0 values corresponding to the no load losses distributed on the three PowerTransformerEnds. The total no load loss shunt impedances may also be placed at one of the PowerTransformerEnds, preferably the end numbered 1, having the shunt values on end 1. This is the preferred way. 4) for a PowerTransformer with more than three Terminals the PowerTransformerEnd impedance values cannot be used. Instead use the TransformerMeshImpedance or split the transformer into multiple PowerTransformers. Each PowerTransformerEnd must be contained by a PowerTransformer. Because a PowerTransformerEnd (or any other object) can not be contained by more than one parent, a PowerTransformerEnd can not have an association to an EquipmentContainer (Substation, VoltageLevel, etc). |  |  | EQ, SC |  |  |  |  | EQ, SC | yes
YES | PowerTransformerEnd | b | Magnetizing branch susceptance (B mag). The value can be positive or negative. | EQ | 1..1 |  |  |  | EQ 1..1 | yes | need to discuss CIM Option 1 and Option 2 with Alan, Chavdar, Ian, Paul. See diagram to right ----> if pick Option 1, need very clear instructions on how the mappings of impedances to windings are done for 3-, 4-, n-winding transformers |  | Schedule 5 - 2W TRANSFORMERS worksheet ...B1 in MVAr for the transformer as a whole Schedule 5 - 3W TRANSFORMERS worksheet ...B1 in MVAr for the transformer as a whole
YES | PowerTransformerEnd | b0 | Zero sequence magnetizing branch susceptance. | SC | 1..1 |  |  |  | SC 1..1 | yes | Option 1 or 2 discussion |  | Schedule 5 - 2W TRANSFORMERS worksheet ...B0 in MVAr for the transformer as a whole Schedule 5 - 3W TRANSFORMERS worksheet ...B0 in MVAr for the transformer as a whole
YES | PowerTransformerEnd | connectionKind | Kind of connection. | EQ | 1..1 | there is probably a correlation between PowerTransformerEnd.connectionKind and TransformerEnd.earthingMethod that should be enforced | realized by cardinality change (from optional to mandatory) | EQ 0..1 | EQ 0..1 | yes |  | p 8 "TABLE 2 - TRANSFORMER DATA …Vector Group" | Schedule 5 - 2W TRANSFORMERS worksheet …HV vector group …LV vector group Schedule 5 - 3W TRANSFORMERS worksheet …HV vector group …MV vector group …LV vector group
YES | PowerTransformerEnd | g | Magnetizing branch conductance. | EQ | 0..1 |  |  |  | EQ 0..1 | yes | examine if needed as part of Option1 or 2 discussion
YES | PowerTransformerEnd | g0 | Zero sequence magnetizing branch conductance (star-model). | SC | 1..1 |  |  |  | SC 1..1 | yes | examine if needed as part of Option1 or 2 discussion
YES | PowerTransformerEnd | phaseAngleClock | Terminal voltage phase angle displacement where 360 degrees are represented with clock hours. The valid values are 0 to 11. For example, for the secondary side end of a transformer with vector group code of 'Dyn11', specify the connection kind as wye with neutral and specify the phase angle of the clock as 11. The clock value of the transformer end number specified as 1, is assumed to be zero. Note the transformer end number is not assumed to be the same as the terminal sequence number. | SC | 1..1 |  |  |  | SC 1..1 | yes |  |  | Schedule 5 - 2W TRANSFORMERS worksheet …LV-Ph. Shift (x 30deg) Schedule 5 - 3W TRANSFORMERS worksheet …MV-Ph. Shift (x 30deg) …LV-Ph. Shift (x 30deg)
YES | PowerTransformerEnd | r | Resistance (star-model) of the transformer end. The attribute shall be equal to or greater than zero for non-equivalent transformers. | EQ | 1..1 |  |  |  | EQ 1..1 | yes | examine if needed as part of Option1 or 2 discussion | p 8 "TABLE 2 - TRANSFORMER DATA …PositiveSequenceImpedance ..R" | Schedule 5 - 2W TRANSFORMERS worksheet …R1 % on 100MVA base
YES | PowerTransformerEnd | r0 | Zero sequence series resistance (star-model) of the transformer end. | SC | 1..1 |  |  |  | SC 1..1 | yes | examine if needed as part of Option1 or 2 discussion |  | Schedule 5 - 2W TRANSFORMERS worksheet …R0 % on 100MVA base
YES | PowerTransformerEnd | ratedS | Normal apparent power rating. The attribute shall be a positive value. For a two-winding transformer the values for the high and low voltage sides shall be identical. | EQ | 1..1 |  |  | EQ 0..1 | EQ 0..1 | yes |  | p 8 "TABLE 2 - TRANSFORMER DATA …TransformerRating" | Schedule 5 - 2W TRANSFORMERS worksheet …Base rating MVA
YES | PowerTransformerEnd | ratedU | Rated voltage: phase-phase for three-phase windings, and either phase-phase or phase-neutral for single-phase windings. A high voltage side, as given by TransformerEnd.endNumber, shall have a ratedU that is greater than or equal to ratedU for the lower voltage sides. The attribute shall be a positive value. | EQ | 1..1 |  |  |  | EQ 1..1 | yes | Note: there is also an association between TransformerEnd and BaseVoltage | p 8 "TABLE 2 - TRANSFORMER DATA …Node 1 ..Voltage ..Node2 ..Voltage" | Schedule 5 - 2W TRANSFORMERS worksheet …node1 V in kV …node2 V in kV
YES | PowerTransformerEnd | x | Positive sequence series reactance (star-model) of the transformer end. | EQ | 1..1 |  |  |  | EQ 1..1 | yes | examine if needed as part of Option1 or 2 discussion | p 8 "TABLE 2 - TRANSFORMER DATA …PositiveSequenceImpedance ..X" | Schedule 5 - 2W TRANSFORMERS worksheet …X1 % on 100MVA base
YES | PowerTransformerEnd | x0 | Zero sequence series reactance of the transformer end. | SC | 1..1 |  |  |  | SC 1..1 | yes | examine if needed as part of Option1 or 2 discussion | p 6 "The main categories of this information shall be listed in the Statement and include: ...Transformers – Zero sequence reactance data" p 8 "TABLE 2 - TRANSFORMER DATA …Zero Sequence Reactance ..X" p 8 "3 Zero sequence reactances should be included for 132kV networks and available on request at other voltage levels" | Schedule 5 - 2W TRANSFORMERS worksheet …X0 % on 100MVA base
EarthingMethodKind <<enumeration>>
| EarthingMethodKind The method of grounding employed on a transformer winding. | [5 empty] | realized by extension and profile change (added class & attributes) | none | none | none
| EarthingMethodKind | Solid | Solid Grounding (LTDS), Solid (GC0139)
| EarthingMethodKind | Resistance | Resistance Grounding (LTDS), Neutral Grounding Resistors (GC0139)
| EarthingMethodKind | Reactance | Reactance Grounding (LTDS)
| EarthingMethodKind | ThroughEarthTransformer | Through Earth Transformer (LTDS), Through Earthing Transformer (GC0139)
| EarthingMethodKind | NotApplicable | Not Applicable (LTDS), Isolated (GC0139)
TransformerCoreAdmittance
IdentifiedObject
| IdentifiedObject | aliasName
| IdentifiedObject | description
| IdentifiedObject | mRID
| IdentifiedObject | name
| TransformerCoreAdmittance The transformer core admittance. Used to specify the core admittance of a transformer in a manner that can be shared among power transformers. | [9 empty] | Option 1 or 2 discussion
| TransformerCoreAdmittance | b | Magnetizing branch susceptance (B mag). The value can be positive or negative. | EQ | 0..1 |  |  |  | none
| TransformerCoreAdmittance | b0 | Zero sequence magnetizing branch susceptance. | SC | 1..1 |  |  |  | none
| TransformerCoreAdmittance | g | Magnetizing branch conductance (G mag). | EQ | 0..1 |  |  |  | none
| TransformerCoreAdmittance | g0 | Zero sequence magnetizing branch conductance. | SC | 1..1 |  |  |  | none
TransformerMeshImpedance
IdentifiedObject
| IdentifiedObject | aliasName
| IdentifiedObject | description
| IdentifiedObject | mRID
| IdentifiedObject | name
| TransformerMeshImpedance Transformer mesh impedance (Delta-model) between transformer ends. The typical case is that this class describes the impedance between two transformer ends pair-wise, i.e. the cardinalities at both transformer end associations are 1. However, in cases where two or more transformer ends are modelled the cardinalities are larger than 1. | [9 empty] | Option 1 or 2 discussion
| TransformerMeshImpedance | r | Resistance between the 'from' and the 'to' end, seen from the 'from' end. | EQ | 1..1 |  |  |  | none |  |  | p 8 "TABLE 2 - TRANSFORMER DATA …PositiveSequenceImpedance ..R" | Schedule 5 - 3W TRANSFORMERS worksheet …M-L R % on 100MVA base …H-M R % on 100MVA base …H-L R % on 100MVA base
| TransformerMeshImpedance | r0 | Zero-sequence resistance between the 'from' and the 'to' end, seen from the 'from' end. | SC | 1..1 |  |  |  | none |  |  |  | Schedule 5 - 3W TRANSFORMERS worksheet …M-L R0 % on 100MVA base …H-M R0 % on 100MVA base …H-L R0 % on 100MVA base
| TransformerMeshImpedance | x | Reactance between the 'from' and the 'to' end, seen from the 'from' end. | EQ | 1..1 |  |  |  | none |  |  | p 8 "TABLE 2 - TRANSFORMER DATA …PositiveSequenceImpedance ..X" | Schedule 5 - 3W TRANSFORMERS worksheet …M-L X % on 100MVA base …H-M X % on 100MVA base …H-L X % on 100MVA base
| TransformerMeshImpedance | x0 | Zero-sequence reactance between the 'from' and the 'to' end, seen from the 'from' end. | SC | 1..1 |  |  |  | none |  |  | p 6 "The main categories of this information shall be listed in the Statement and include: ...Transformers – Zero sequence reactance data" p 8 "TABLE 2 - TRANSFORMER DATA …Zero Sequence Reactance ..X" p 8 "3 Zero sequence reactances should be included for 132kV networks and available on request at other voltage levels" | Schedule 5 - 3W TRANSFORMERS worksheet …M-L X0 % on 100MVA base …H-M X0 % on 100MVA base …H-L X0 % on 100MVA base

## EQ SC SSH - ShuntCompensator
Class | Parent Class or Class | Attribute | Description (CIM Notes) | LTDS Profile | LTDS UML Constraint | LTDS Additional Constraints | In CGMES 3.0 profile | In 61970-452 Ed4 EQ, SC, OP or 61970-456 Ed3 SSH profiles | In CIM information model | Comments / Questions | Existing LTDS requirement | Proposed GC0139 requirement
ShuntCompensator
IdentifiedObject
| IdentifiedObject | aliasName
| IdentifiedObject | description
| IdentifiedObject | mRID
| IdentifiedObject | name
PowerSystemResource
Equipment
| Equipment | aggregate
| Equipment | inService
| Equipment | networkAnalysisEnabled
| Equipment | normallyInService
ConductingEquipment
EnergyConnection
RegulatingCondEq
| RegulatingCondEq | controlEnabled
| ShuntCompensator A shunt capacitor or reactor or switchable bank of shunt capacitors or reactors. A section of a shunt compensator is an individual capacitor or reactor. A negative value for bPerSection indicates that the compensator is a reactor. ShuntCompensator is a single terminal device. Ground is implied. |  |  | EQ, SC, SSH |  |  |  | EQ, SC, SSH | yes | no requirement in existing LTDS asking LTDS WG for input
| ShuntCompensator | aVRDelay | An automatic voltage regulation delay (AVRDelay) which is the time delay from a change in voltage to when the capacitor is allowed to change state. This filters out temporary changes in voltage. | EQ | 0..1 |  |  | EQ 0..1 | yes
| ShuntCompensator | grounded | Used for Yn and Zn connections. True if the neutral is solidly grounded. | EQ | 0..1 | required if phaseConnection=Yn or Zn, else no attribute |  | EQ 0..1 | yes
| ShuntCompensator | maximumSections | The maximum number of sections that may be switched in. | EQ | 1..1 |  |  | EQ 1..1 | yes
| ShuntCompensator | nomU | The voltage at which the nominal reactive power may be calculated. This should normally be within 10% of the voltage at which the capacitor is connected to the network. | EQ | 1..1 |  |  | EQ 1..1 | yes
| ShuntCompensator | normalSections | The normal number of sections switched in. The value shall be between zero and ShuntCompensator.maximumSections. | EQ | 1..1 |  |  | EQ 1..1 | yes
| ShuntCompensator | phaseConnection | The type of phase connection, such as wye or delta. |  |  |  |  | none | yes
| ShuntCompensator | sections | Shunt compensator sections in use. Starting value for steady state solution. The attribute shall be a positive value or zero. Non integer values are allowed to support continuous variables. The reasons for continuous value are to support study cases where no discrete shunt compensators has yet been designed, a solutions where a narrow voltage band force the sections to oscillate or accommodate for a continuous solution as input. For LinearShuntConpensator the value shall be between zero and ShuntCompensator.maximumSections. At value zero the shunt compensator conductance and admittance is zero. Linear interpolation of conductance and admittance between the previous and next integer section is applied in case of non-integer values. For NonlinearShuntCompensator(-s) shall only be set to one of the NonlinearShuntCompenstorPoint.sectionNumber. There is no interpolation between NonlinearShuntCompenstorPoint(-s). | SSH | 1..1 |  |  | SSH 1..1 | yes
| ShuntCompensator | voltageSensitivity | Voltage sensitivity required for the device to regulate the bus voltage, in voltage/reactive power. | EQ | 0..1 |  |  | EQ 0..1 | yes
LinearShuntCompensator
IdentifiedObject
| IdentifiedObject | aliasName
| IdentifiedObject | description
| IdentifiedObject | mRID
| IdentifiedObject | name
PowerSystemResource
Equipment
| Equipment | aggregate
| Equipment | inService
| Equipment | networkAnalysisEnabled
| Equipment | normallyInService
ConductingEquipment
EnergyConnection
RegulatingCondEq
| RegulatingCondEq | controlEnabled
ShuntCompensator
| ShuntCompensator | aVRDelay |  | EQ | 0..1
| ShuntCompensator | grounded |  | EQ | 0..1
| ShuntCompensator | maximumSections |  | EQ | 1..1
| ShuntCompensator | nomU |  | EQ | 1..1
| ShuntCompensator | normalSections |  | EQ | 1..1
| ShuntCompensator | phaseConnection |  | 0 | 0
| ShuntCompensator | sections |  | SSH | 1..1
| ShuntCompensator | voltageSensitivity |  | EQ | 0..1
| LinearShuntCompensator A linear shunt compensator has banks or sections with equal admittance values. |  |  | EQ, SC, SSH |  |  |  | EQ, SC, SSH | yes | no requirement in existing LTDS asking LTDS WG for input
| LinearShuntCompensator | b0PerSection | Zero sequence shunt (charging) susceptance per section. |  |  | applies only to shunt reactors |  | SC 1..1 | yes
| LinearShuntCompensator | bPerSection | Positive sequence shunt (charging) susceptance per section. |  |  |  |  | EQ 1..1 | yes
| LinearShuntCompensator | g0PerSection | Zero sequence shunt (charging) conductance per section. |  |  | applies only to shunt reactors |  | SC 1..1 | yes
| LinearShuntCompensator | gPerSection | Positive sequence shunt (charging) conductance per section. |  |  |  |  | EQ 1..1 | yes
NonLinearShuntCompensator
IdentifiedObject
| IdentifiedObject | aliasName
| IdentifiedObject | description
| IdentifiedObject | mRID
| IdentifiedObject | name
PowerSystemResource
Equipment
| Equipment | aggregate
| Equipment | inService
| Equipment | networkAnalysisEnabled
| Equipment | normallyInService
ConductingEquipment
EnergyConnection
RegulatingCondEq
| RegulatingCondEq | controlEnabled
ShuntCompensator
| ShuntCompensator | aVRDelay |  | EQ | 0..1
| ShuntCompensator | grounded |  | EQ | 0..1
| ShuntCompensator | maximumSections |  | EQ | 1..1
| ShuntCompensator | nomU |  | EQ | 1..1
| ShuntCompensator | normalSections |  | EQ | 1..1
| ShuntCompensator | phaseConnection |  | 0 | 0
| ShuntCompensator | sections |  | SSH | 1..1
| ShuntCompensator | voltageSensitivity |  | EQ | 0..1
| NonLinearShuntCompensator A non linear shunt compensator has bank or section admittance values that differ. The attributes g, b, g0 and b0 of the associated NonlinearShuntCompensatorPoint describe the total conductance and admittance of a NonlinearShuntCompensatorPoint at a section number specified by NonlinearShuntCompensatorPoint.sectionNumber. |  |  | EQ, SSH |  |  |  | EQ, SSH | yes | no requirement in existing LTDS asking LTDS WG for input
NonLinearShuntCompensatorPoint
| NonLinearShuntCompensatorPoint A non linear shunt compensator bank or section admittance value. The number of NonlinearShuntCompenstorPoint instances associated with a NonlinearShuntCompensator shall be equal to ShuntCompensator.maximumSections. ShuntCompensator.sections shall only be set to one of the NonlinearShuntCompenstorPoint.sectionNumber. There is no interpolation between NonlinearShuntCompenstorPoint-s. |  |  | EQ, SC |  |  |  | EQ, SC | yes | no requirement in existing LTDS asking LTDS WG for input
| NonLinearShuntCompensatorPoint | b | Positive sequence shunt (charging) susceptance per section. |  |  |  |  | EQ 1..1
|  | b0 | Zero sequence shunt (charging) susceptance per section. |  |  |  |  | SC 1..1
|  | g | Positive sequence shunt (charging) conductance per section. |  |  |  |  | EQ 1..1
|  | g0 | Zero sequence shunt (charging) conductance per section. |  |  |  |  | SC 1..1
|  | sectionNumber | The number of the section. |  |  |  |  | EQ 1..1
StaticVarCompensator
IdentifiedObject
| IdentifiedObject | aliasName
| IdentifiedObject | description
| IdentifiedObject | mRID
| IdentifiedObject | name
PowerSystemResource
Equipment
| Equipment | aggregate
| Equipment | inService
| Equipment | networkAnalysisEnabled
| Equipment | normallyInService
ConductingEquipment
EnergyConnection
RegulatingCondEq
| RegulatingCondEq | controlEnabled
| StaticVarCompensator A facility for providing variable and controllable shunt reactive power. The SVC typically consists of a stepdown transformer, filter, thyristor-controlled reactor, and thyristor-switched capacitor arms. The SVC may operate in fixed MVar output mode or in voltage control mode. When in voltage control mode, the output of the SVC will be proportional to the deviation of voltage at the controlled bus from the voltage setpoint. The SVC characteristic slope defines the proportion. If the voltage at the controlled bus is equal to the voltage setpoint, the SVC MVar output is zero. |  |  | EQ, SSH |  |  |  | EQ, SC, SSH | yes | no requirement in existing LTDS asking LTDS WG for input
| StaticVarCompensator | capacitiveRating | Capacitive reactance at maximum capacitive reactive power. Shall always be positive. |  |  |  |  | EQ 1..1 | yes
| StaticVarCompensator | inductiveRating | Inductive reactance at maximum inductive reactive power. Shall always be negative. |  |  |  |  | EQ 1..1 | yes
| StaticVarCompensator | q | Reactive power injection. Load sign convention is used, i.e. positive sign means flow out from a node. Starting value for a steady state solution. |  |  |  |  | SSH 1..1 | yes
| StaticVarCompensator | slope | The characteristics slope of an SVC defines how the reactive power output changes in proportion to the difference between the regulated bus voltage and the voltage setpoint. The attribute shall be a positive value or zero. |  |  |  |  | EQ 1..1 | yes
| StaticVarCompensator | sVCControlMode | SVC control mode. |  |  |  |  | EQ 1..1 | yes
| StaticVarCompensator | voltageSetPoint | The reactive power output of the SVC is proportional to the difference between the voltage at the regulated bus and the voltage setpoint. When the regulated bus voltage is equal to the voltage setpoint, the reactive power output is zero. |  |  |  |  | EQ 1..1 | yes

## EQ SSH - OperationalLimitSet
Class | Parent Class or Class | Attribute | Description (CIM Notes) | LTDS Profile | LTDS UML Constraint | LTDS Additional Constraints | Change from CGMES 3.0 | In CGMES 3.0 profile | In 61970-452 Ed4 EQ, SC, OP or 61970-456 Ed3 SSH profiles | In CIM information model | Comments / Questions | Existing LTDS requirement | Proposed GC0139 requirement
Instance Requirements |  |  | General philosophy: a reference to an OperationalLimitSet is required for every line, every transformer (and every winding of 3-winding transformer), and for every bus section that can be individually de-energized Mandatory For lines - a unique line limit OperationalLimitSet must be associated with a Terminal of one of the ACLineSegments making up Line. The limits reflect the ratings of all equipment in the series path of the ACLineSegments, plus any substation equipment considered in the DNO's standard limit calculcation. - for 132 kV lines, the line limit OperationalLimitSet shall be comprised of a CurrentLimit for summer, a CurrentLimit for winter, and a CurrentLimit for spring/autumn. - for other lines, the line limit OperationalLimitSet shall be comprised of a continuous CurrentLimit and an emergency CurrentLimit. - the description field of the line limit OperationalLimitSet shall be used to provide any information necessary for interpretation of the line's OperationalLimitSet. - line limits are expressed in Amps. For transformers - for 2-winding transformers, a single, unique transformer OperationalLimitSet must be associated with the Terminal of the higher voltage winding. The limits reflect the limitations of both windings. - for 3-winding transformers, a single, unique transformer OperationalLimitSet must be associated with the Terminal of each winding. - the transformer OperationalLimitSet shall be comprised of an ApparentPowerLimit for summer and an ApparentPowerLimit for winter. - transformer limits are expressed in MVA. For busses - a unique bus voltage OperationalLimitSet must be associated with the Terminal of every BusbarSection. - the OperationalLimitSet shall be comprised of a high VoltageLimit and a low VoltageLimit. Allowed - |  |  |  | none |  |  |  | Significant expansion of LTDS requirements: - Circuits now have set of 2 or 3 operational limits (depending on voltage level) instead of a single rating - Transformers now have a 2 operational limits instead of a single rating and, for 3-winding transformers, limits are required for each winding - High and low voltage limits are required for every bus instead of a single designation of "bandwidth for each voltage level in the distribution system" The increase in requirements is intended to allow modeling to better support use in network analysis studies. | Single rating for whole transformer, single rating for circuit, bandwidth for each voltage level (presumably at a system level)
Unsatisfied requirements |  |  | Is reverse flow best expressed as an additional operational limit (in MVA) or as a %age of a winding's rating? Use diagram in discussion.
OperationalLimitSet
IdentifiedObject
| IdentifiedObject | aliasName
| IdentifiedObject | description
AUTO | IdentifiedObject | mRID
YES | IdentifiedObject | name
| OperationalLimitSet A set of limits associated with equipment. Sets of limits might apply to a specific temperature, or season for example. A set of limits may contain different severities of limit levels that would apply to the same equipment. The set may contain limits of different types such as apparent power and current limits or high and low voltage limits that are logically applied together as a set. |  |  | EQ |  |  |  |  | EQ | yes
OperationalLimit
IdentifiedObject
| IdentifiedObject | aliasName
| IdentifiedObject | description
| IdentifiedObject | mRID
| IdentifiedObject | name
| OperationalLimit A value and normal value associated with a specific kind of limit. The sub class value and normalValue attributes vary inversely to the associated OperationalLimitType.acceptableDuration (acceptableDuration for short). If a particular piece of equipment has multiple operational limits of the same kind (apparent power, current, etc.), the limit with the greatest acceptableDuration shall have the smallest limit value and the limit with the smallest acceptableDuration shall have the largest limit value. Note: A large current can only be allowed to flow through a piece of equipment for a short duration without causing damage, but a lesser current can be allowed to flow for a longer duration. |  |  | EQ, SSH |  |  |  |  | EQ, SSH | yes
ApparentPowerLimit
IdentifiedObject
| IdentifiedObject | aliasName
| IdentifiedObject | description
AUTO | IdentifiedObject | mRID
YES | IdentifiedObject | name
OperationalLimit
| ApparentPowerLimit Apparent power limit. |  |  | EQ, SSH |  |  |  |  | EQ, SSH | yes | LTDS and GC0139 have only a single rating on transformer. Does it make sense to use an OperationalLimitSet or not? | p 8 "TABLE 2 - TRANSFORMER DATA …Transformer Rating" p 8 "TABLE 2 - TRANSFORMER DATA …Reverse PowerCapability" p 8 "5 If the reverse power capability of a transformer has not been assessed, this should be shown as "NOT KNOWN" in this table" | Schedule 5 - LINES worksheet ...MVA ratings for Winter, Spring, Summer, Autumn
YES | ApparentPowerLimit | normalValue | The normal apparent power limit. The attribute shall be a positive value or zero. | [5 empty] | EQ 1..1 | yes
| ApparentPowerLimit | value | The apparent power limit. The attribute shall be a positive value or zero. | [5 empty] | SSH 1..1 | yes
ActivePowerLimit
IdentifiedObject
| IdentifiedObject | aliasName
| IdentifiedObject | description
| IdentifiedObject | mRID
| IdentifiedObject | name
OperationalLimit
| ActivePowerLimit Limit on active power flow. |  |  | EQ, SSH |  |  |  |  | EQ, SSH | yes | not yet a requirement for active power in LTDS. if still true when all types of data have been modeled, consider deleting class from profile
| ActivePowerLimit | normalValue | The normal value of active power limit. The attribute shall be a positive value or zero. | [5 empty] | EQ 1..1 | yes
| ActivePowerLimit | value | Value of active power limit. The attribute shall be a positive value or zero. | [5 empty] | SSH 1..1 | yes
CurrentLimit
IdentifiedObject
| IdentifiedObject | aliasName
| IdentifiedObject | description
AUTO | IdentifiedObject | mRID
YES | IdentifiedObject | name
OperationalLimit
| CurrentLimit Operational limit on current. |  |  | EQ, SSH |  | 3 CurrentLimits required for OperationalLimitSets associated with a Terminal of an ACLineSegment associated with BaseVoltage whose .nominalVoltage =132, 2 CurrentLimits required for OperationalLimitSets associated with Terminal of other ACLineSegments |  |  | EQ, SSH | yes |  | p 7 "TABLE 1 - CIRCUIT DATA …Rating Information ...Amps or MVA" p 7 "Rating information that is used by the licensee should be provided together with any explanatory note required to assist a user to interpret the information."
YES | CurrentLimit | normalValue | The normal value for limit on current flow. The attribute shall be a positive value or zero. | EQ 1..1 |  |  |  |  | EQ 1..1 | yes
| CurrentLimit | value | Limit on current flow. The attribute shall be a positive value or zero. | [5 empty] | SSH 1..1 | yes
VoltageLimit
IdentifiedObject
| IdentifiedObject | aliasName
| IdentifiedObject | description
AUTO | IdentifiedObject | mRID
YES | IdentifiedObject | name
OperationalLimit
| VoltageLimit Operational limit applied to voltage. The use of operational VoltageLimit is preferred instead of limits defined at VoltageLevel. The operational VoltageLimits are used, if present. |  |  | EQ, SSH |  | 2 VoltageLimits required for OperationalLimitSets associated with Terminal of BusbarSection |  |  | EQ, SSH | yes |  | p 5 "General network characteristics including descriptions of: …. Operating voltages (target and bandwidth) for each voltage level of the distribution network" p 5 "General network characteristics including descriptions of: …. Operating voltages (target and bandwidth) for each voltage level of the distribution network" p 7 "TABLE 1 - CIRCUIT DATA …Operating Voltage" p 8 "TABLE 2 - TRANSFORMER DATA …Node 1 ..Voltage ..Node 2 ..Voltage" p 9 "TABLE 3 - LOAD INFORMATION …Voltage Level" p 10 "TABLE 4 - FAULT LEVEL INFORMATION …Voltage Level"
YES | VoltageLimit | normalValue | The normal limit on voltage. High or low limit nature of the limit depends upon the properties of the operational limit type. The attribute shall be a positive value or zero. | EQ 1..1 |  | of the 2 VoltageLimit instances associated with an OperationalLimitSet, the value of .normalValue must be larger for the VoltageLimit associated with an OperationalLimitType with .direction=high than the value of .normalValue for the other VoltageLimit (which will be associated with an OperationalLimitType with .direction =low) |  |  | EQ 1..1 | yes
| VoltageLimit | value | Limit on voltage. High or low limit nature of the limit depends upon the properties of the operational limit type. The attribute shall be a positive value or zero. | [5 empty] | SSH 1..1 | yes
OperationalLimitType
| IdentifiedObject | [9 empty] | 14400
| IdentifiedObject | aliasName
| IdentifiedObject | description
AUTO | IdentifiedObject | mRID
YES | IdentifiedObject | name |  |  |  | possible values: In EQ: - for line limits 132kV Circuit Winter Limit 132kV Circuit Spring/Autumn Limit 132kV Circuit Summer Limit <132kV Circuit Continuous Limit <132kV Circuit Emergency Limit - for transformers limits Xf Winter Limit Xf Summer Limit Xf Reverse Limit (maybe) - for bus voltage limits Bus Voltage High Limit Bus Voltage Low Limit
| OperationalLimitType The operational meaning of a category of limits. |  |  | EQ |  |  |  |  | EQ | yes |  | p 5 "General network characteristics including descriptions of: …. Operating voltages (target and bandwidth) for each voltage level of the distribution network"
OPTIONAL | OperationalLimitType | acceptableDuration | The nominal acceptable duration of the limit. Limits are commonly expressed in terms of the time limit for which the limit is normally acceptable. The actual acceptable duration of a specific limit may depend on other local factors such as temperature or wind speed. The attribute has meaning only if the flag isInfiniteDuration is set to false, hence it shall not be exchanged when isInfiniteDuration is set to true. | EQ | 0..1 | for .name= <132kV Circuit Emergency Limit, .acceptableDuration must = 14400 seconds (4 hours), otherwise, attribute shall not be present |  |  | EQ 0..1 | yes
YES | OperationalLimitType | direction | The direction of the limit. | EQ | 1..1 | for .name = 132kV Circuit Winter Limit 132kV Circuit Spring/Autumn Limit 132kV Circuit Summer Limit <132kV Circuit Continuous Limit <132kV Circuit Emergency Limit .direction must =absoluteValue for .name = Xf Winter Limit Xf Summer Limit Xf Reverse Limit (maybe) Bus Voltage High Limit .direction must =high for .name =Bus Voltage Low Limit .direction must =low |  |  | EQ 1..1 | yes | Pat: omgosh.. I just didn't see 'absoluteValue' duh. .direction=absoluteValue should work for the line limits which are in Amps and must be zero or positive. For ACLineSegments, monitored/state variable values would be either + or - depending on direction of real power flow but either way the absolute value of the monitored value would be compared to the limit. the bus voltage limits work OK with .direction=high for the high limit and low for the low limit For winter/summer 'normal direction' transformer limits in MVA work with .direction=high, but only because MVA is always positive. If we implement the OperationalLimitType of Xf Reverse Limit there would have to be logic that said: - for the high voltage winding, when MW (real power) is + (into the transformer end) use the Xf Winter Limit or the Xf Summer Limit and when MW is - (out of the transformer end into the high voltage system) use the Xf Reverse Limit - for the low voltage winding(s), when MW is - (out of the transformer end into the lower voltage bus(es), use the Xf Winter Limit or the Xf Summer Limit and when MW is + (into the transformer end) use the Xf Reverse Limit
YES | OperationalLimitType | isInfiniteDuration | Defines if the operational limit type has infinite duration. If true, the limit has infinite duration. If false, the limit has definite duration which is defined by the attribute acceptableDuration. | EQ | 1..1 | for .name= <132kV Circuit Emergency Limit, .isInfiniteDuration must = false, otherwise .isInfiniteDuration must =true |  |  | EQ 1..1 | yes

## EQ SC SSH - Containment
Class | Parent Class or Class | Attribute | Description (CIM Notes) | LTDS Profile | LTDS UML Constraint | LTDS Additional Constraints | Change from CGMES 3.0 | In CGMES 3.0 profile | In 61970-452 Ed4 EQ, SC, OP or 61970-456 Ed3 SSH profiles | In 61968-13 Ed 2 Functional profile | In CIM information model | Comments / Questions | Existing LTDS requirement | Proposed GC0139 requirement
Instance Requirements |  |  | General Philosophy for containment: All ConductingEquipment is contained in Lines or (directly or indirectly) in Substations Mandatory - Every ConductingEquipment is contained in either a Line or (directly or indirectly) in a Substation and uses the EquipmentContainer association to describe its containment - Every ConductingEquipment within the substation fence is (either directly or indirectly) contained in Substation Allowed - Substation ConductingEquipment which is also functionally related to a line may be associated to Line using the AdditionalEquipmentContainer association General Philosophy for 'regions': Basic modeling of licence regions and GSPs is done consistently across all DNOs. Smaller containers can be modeled at the discretion of DNOs. Mandatory - Each DNO licence region is modeled with a GridRegion containing a GridRegion for each of its GSPs - Each GSP GridRegion is associated with its supplying Substation(s) and each GSP GridRegion contains (either directly or indirectly) the appropriate Substations and the appropriate Lines Allowed - Use of additional GridRegions for smaller nested groupings of substations and lines within a GSP GridRegion, which may or may not include an indication of supplying Substation(s) |  |  |  | The two 'region' containers (GeographicalRegion and SubGeographicalRegion) do not align well with UK needs and for LTDS, so an extension providing multiple levels of containment, each with one or more supplying substations, is proposed. This resulted in the removal of 2 classes from the EQ profile and the creation of a new class and a new enumerated class in the information model and their addition to the EQ profile. |  |  |  |  | Little change to existing LTDS: - information structured differently but content is essentially the same | GSP is used to organize table information and to group Node IDs
Unsatisfied requirements
GeographicalRegion | [11 empty] | Chavdar: before removing and adding it will be good to see if we can reuse formthing form ENTSO-E extensions and adapt. We have required associations from Substation in 452 and CGMES which it will be hard to touch at this point as this will create confusion in existing tools
IdentifiedObject
| IdentifiedObject | aliasName
| IdentifiedObject | description
| IdentifiedObject | mRID
| IdentifiedObject | name
| GeographicalRegion A geographical region of a power system network model. |  |  | none |  |  | realized by profile change (removed class) | EQ | EQ | Functional | yes | remove from profile (is replaced with new GridRegion model) --->
SubGeographicalRegion
IdentifiedObject
| IdentifiedObject | aliasName
| IdentifiedObject | description
| IdentifiedObject | mRID
| IdentifiedObject | name
| SubGeographicalRegion A subset of a geographical region of a power system network model. |  |  | none |  |  | realized by profile change (removed class) | EQ | EQ | Functional | yes | remove from profile (is replaced with new GridRegion model) --->
GridRegion
IdentifiedObject
| IdentifiedObject | aliasName
| IdentifiedObject | description
AUTO | IdentifiedObject | mRID
YES | IdentifiedObject | name
| GridRegion A region of the grid that contains substations, lines and other grid regions. A grid region aids in organizing the equipment of the grid for human understanding. It is used to suppport display navigation, equipment naming, and interaction with field crews. While a grid region is often reflective of connectivity, connectivity cannot be inferred from it. |  |  | EQ |  |  |  | none | none | none | no |  | p 7 "TABLE 1 - CIRCUIT DATA …S/S Group" p 8 "TABLE 2 - TRANSFORMER DATA …S/S Group" p 9 "TABLE 3 - LOAD INFORMATION …S/S Group" p 10 "TABLE 4 - FAULT LEVEL INFORMATION …S/S Group" p 11 "TABLE 5 - GENERATION ...S/S Group (Grid Supply Point)" p 13 "TABLE 6 - TABLE OF INTEREST IN A CONNECTION ...Grid supply point"
YES | GridRegion | regionKind | The kind of grid region, for example, Grid Supply Point or licence region. | EQ | 0..1 |  | realized by extension and profile change (added class and attribute) | none | none | none | no
GridRegionKind <<enumeration>>
| GridRegionKind The kind of grid region. |  |  | EQ |  |  | realized by extension and profile change (added class & attributes) | none | none | none | no
| EarthingMethodKind | licenceRegion | Solid Grounding (LTDS), Solid (GC0139)
| EarthingMethodKind | GSP | Resistance Grounding (LTDS), Neutral Grounding Resistors (GC0139)
ConnectivityNode>EquipmentContainer
IdentifiedObject
| IdentifiedObject | aliasName
| IdentifiedObject | description
| IdentifiedObject | mRID
| IdentifiedObject | name
PowerSystemResource
| ConnectivityNodeContainer A base class for all objects that may contain connectivity nodes or topological nodes. |  |  | EQ |  |  |  |  | EQ | Functional | yes
| EquipmentContainer A modelling construct to provide a root class for containing equipment. |  |  | EQ |  | Every ConductingEquipment shall be associated with an EquipmentContainer |  |  | EQ | Functional | yes | does the constraint make sense? Anything else that should be in the EquipmentContainer? AuxiliaryEquipment maybe?
Line
IdentifiedObject
| IdentifiedObject | aliasName
| IdentifiedObject | description
AUTO | IdentifiedObject | mRID
YES | IdentifiedObject | name
PowerSystemResource
ConnectivityNodeContainer
EquipmentContainer
| Line Contains equipment beyond a substation belonging to a power transmission line. |  |  | EQ |  |  |  |  | EQ | Functional | yes
Substation
IdentifiedObject
| IdentifiedObject | aliasName
| IdentifiedObject | description
AUTO | IdentifiedObject | mRID
YES | IdentifiedObject | name
PowerSystemResource
| ConnectivityNodeContainer |  |  |  |  | :
EquipmentContainer
| Substation A collection of equipment for purposes other than generation or utilization, through which electric energy in bulk is passed for the purposes of switching or modifying its characteristics. |  |  | EQ |  |  |  |  | EQ | Functional | yes |  | p 7 "TABLE 1 - CIRCUIT DATA …S/S or Busbar Name" p 8 "TABLE 2 - TRANSFORMER DATA …S/S or Busbar Name" p 9 "TABLE 3 - LOAD INFORMATION …S/S or Busbar Name" p 10 "TABLE 4 - FAULT LEVEL INFORMATION …S/S or Busbar Name" p 11 "TABLE 5 - GENERATION ...Supply Point ..Primary Substation" p 13 "TABLE 6 - TABLE OF INTEREST IN A CONNECTION ...Supply Point ..Primary Substation"
Bay
IdentifiedObject
| IdentifiedObject | aliasName
| IdentifiedObject | description
AUTO | IdentifiedObject | mRID
YES | IdentifiedObject | name
PowerSystemResource
ConnectivityNodeContainer
EquipmentContainer
| Bay A collection of power system resources (within a given substation) including conducting equipment, protection relays, measurements, and telemetry. A bay typically represents a physical grouping related to modularization of equipment. |  |  | EQ |  | PowerTransformer shall not be contained in a Bay Every Bay shall be contained in a VoltageLevel |  |  | EQ | Functional | yes | is there a universally understood meaning for 'Bay' in the UK? For example, would everyone know where the containment boundaries would be on the 132, 133, 6.6 kV subsations to the right? ---> any ConductingEquipment that should be directly in Bay?
| Bay | bayEnergyMeasFlag | Indicates the presence/absence of energy measurements. | none |  |  |  |  | none | none | yes
| Bay | bayPowerMeasFlag | Indicates the presence/absence of active/reactive power measurements. | none |  |  |  |  | none | none | yes
| Bay | breakerConfiguration | Breaker configuration. | none |  |  |  |  | none | Functional 0..1 | yes
| Bay | busBarConfiguration | Busbar configuration. | none |  |  |  |  | none | none | yes
VoltageLevel
IdentifiedObject
| IdentifiedObject | aliasName
| IdentifiedObject | description
AUTO | IdentifiedObject | mRID
YES | IdentifiedObject | name
PowerSystemResource
ConnectivityNodeContainer
EquipmentContainer
| VoltageLevel A collection of equipment at one common system voltage forming a switchgear. The equipment typically consists of breakers, busbars, instrumentation, control, regulation and protection devices as well as assemblies of all these. |  |  | EQ |  | PowerTransformer shall not be contained in a VoltageLevel Every VoltageLevel shall be contained in a Substation |  |  | EQ | Functional | yes | any ConductingEquipment that should be directly in VoltageLevel?
| VoltageLevel | highVoltageLimit | The bus bar's high voltage limit. The limit applies to all equipment and nodes contained in a given VoltageLevel. It is not required that it is exchanged in pair with lowVoltageLimit. It is preferable to use operational VoltageLimit, which prevails, if present. | none |  |  | realized by profile change (removed attribute) | EQ 0..1 | EQ 0..1 | none | yes
| VoltageLevel | lowVoltageLimit | The bus bar's low voltage limit. The limit applies to all equipment and nodes contained in a given VoltageLevel. It is not required that it is exchanged in pair with highVoltageLimit. It is preferable to use operational VoltageLimit, which prevails, if present. | none |  |  | realized by profile change (removed attribute) | EQ 0..1 | EQ 0..1 | none | yes

## GL - Geo Location
Class | Parent Class or Class | Attribute | Description (CIM Notes) | LTDS Profile | LTDS UML Constraint | LTDS Additional Constraints | Change from CGMES 3.0 | In CGMES 3.0 profile | In 61968-13 Ed 2 Geographical profile | In CIM information model | Comments / Questions | Existing LTDS requirement | Proposed GC0139 requirement
Instance Requirements |  |  | General Philosophy: Every substation has a geo-location; every ConductingEquipment outside a substation has a geo-location Mandatory - Every ConductingEquipment not associated (directly or indirectly) with a Substation has a Location and every Substation has a Location Allowed - Specification of the geo-extent of any GridRegion (licence region, GSP or other) - Specification of z-axis (height) on any Location |  |  |  | Lack of an LTDS requirement for physical address information resulted in an attribute being removed from ?GL? profile. |  |  |  | Small expansion to existing LTDS: - the kinds of objects for which geo-location is to be supplied remain the same (substations and circuits). - revised LTDS calls for geo-location of those HV substations and HV circuits which are within LTDS model scope. | "approximate locations of 132kV and EHV circuits and substations are shown on geographic plan(s)"
Unsatisfied requirements |  |  | Should geo-extents of GridRegions (licence region, GSP or other) be required?
IdentifiedObject
| IdentifiedObject This is a root class to provide common identification for all classes needing identification and naming attributes. |  |  | GL |  |  |  |  | Geographical | yes
| IdentifiedObject | aliasName | The aliasName is free text human readable name of the object alternative to IdentifiedObject.name. It may be non unique and may not correlate to a naming hierarchy. The attribute aliasName is retained because of backwards compatibility between CIM releases. It is however recommended to replace aliasName with the Name class as aliasName is planned for retirement at a future time. | none |  |  |  |  | Geographical 0..1 | yes
| IdentifiedObject | description | The description is a free human readable text describing or naming the object. It may be non unique and may not correlate to a naming hierarchy. | none |  |  |  |  | Geographical 0..1 | yes
| IdentifiedObject | mRID | Master resource identifier issued by a model authority. The mRID is unique within an exchange context. Global uniqueness is easily achieved by using a UUID, as specified in IETF RFC 4122, for the mRID. The use of UUID is strongly recommended. For CIMXML data files in RDF syntax conforming to IEC 61970-552, the mRID is mapped to rdf:ID or rdf:about attributes that identify CIM object elements. | GL | 1..1 |  |  |  | Geographical 0..1 | yes
| IdentifiedObject | name | The name is any free human readable and possibly non unique text naming the object. | GL | 0..1 |  |  |  | Geographical 0..1 | yes
Location
IdentifiedObject
| IdentifiedObject | aliasName |  | none | 0
| IdentifiedObject | description |  | none | 0
AUTO | IdentifiedObject | mRID |  | GL | 1..1
YES | IdentifiedObject | name |  | GL | 0..1
| Location The place, scene, or point of something where someone or something has been, is, and/or will be at a given moment in time. It can be defined with one or more position points (coordinates) in a given coordinate system. |  |  | GL |  |  |  |  | Geographical | yes |  | p 5 "approximate locations of 132kV and EHV circuits and substations are shown on geographic plan(s)"
| Location | direction | (if applicable) Direction that allows field crews to quickly find a given asset. For a given location, such as a street address, this is the relative direction in which to find the asset. For example, a streetlight may be located at the 'NW' (northwest) corner of the customer's site, or a usage point may be located on the second floor of an apartment building. | none |  |  |  |  | none | yes
| Location | electronicAddress | Electronic address. | none |  |  |  |  | none | yes
| Location | geoInfoReference | (if applicable) Reference to geographical information source, often external to the utility. | none |  |  |  |  | none | yes
| Location | mainAddress | Main address of the location. | none |  |  | realized by profile change (removed attribute) | ?GL? 0..1 | Geographical 0..1 | yes | can we get rid of this attribute - I'm guessing this was for Substation - which could be important for Operations, maybe, but seems unnecessary for LTDS
| Location | phone1 | Phone number. | none |  |  |  |  | none | yes
| Location | phone2 | Additional phone number. | none |  |  |  |  | none | yes
| Location | secondaryAddress | Secondary address of the location. For example, PO Box address may have different ZIP code than that in the 'mainAddress'. | none |  |  |  |  | none | yes
| Location | status | Status of this location. | none |  |  |  |  | none | yes
| Location | type | Classification by utility's corporate standards and practices, relative to the location itself (e.g., geographical, functional accounting, etc., not a given property that happens to exist at that location). | none |  |  |  |  | none | yes
CoordinateSystem
IdentifiedObject
| IdentifiedObject | aliasName |  | none | 0
| IdentifiedObject | description |  | none | 0
AUTO | IdentifiedObject | mRID |  | GL | 1..1
YES | IdentifiedObject | name |  | GL | 0..1
| CoordinateSystem Coordinate reference system. |  |  | GL |  |  |  |  | Geographical | yes
YES | CoordinateSystem | crsUrn | A Uniform Resource Name (URN) for the coordinate reference system (crs) used to define 'Location.PositionPoints'. An example would be the European Petroleum Survey Group (EPSG) code for a coordinate reference system, defined in URN under the Open Geospatial Consortium (OGC) namespace as: urn:ogc:def:crs:EPSG::XXXX, where XXXX is an EPSG code (a full list of codes can be found at the EPSG Registry web site http://www.epsg-registry.org/). To define the coordinate system as being WGS84 (latitude, longitude) using an EPSG OGC, this attribute would be urn:ogc:def:crs:EPSG::4236. A profile should limit this code to a set of allowed URNs agreed to by all sending and receiving parties. | GL | 1..1 | shall be =urn:ogc:def:crs:EPSG::4236 |  |  | Geographical 1..1 | yes | this specifies using Latitude/Longitude in Decimal Degrees
PositionPoint
| PositionPoint Set of spatial coordinates that determine a point, defined in the coordinate system specified in 'Location.CoordinateSystem'. Use a single position point instance to describe a point-oriented location. Use a sequence of position points to describe a line-oriented object (physical location of non-point oriented objects like cables or lines), or area of an object (like a substation or a geographical zone - in this case, have first and last position point with the same values). |  |  | GL |  | Locations associated with ACLineSegments shall have at least 2 PositionPoints and may have an unlimited number. Locations associated with Substations can have 1 or more PositionPoints. Locations associated with other PowerSystemResources shall have 1 PositionPoint. |  |  | Geographical | yes
| PositionPoint | groupNumber | Zero-relative sequence number of this group within a series of points; used when there is a need to express disjoint groups of points that are considered to be part of a single location. | none |  |  |  |  | none | yes
YES | PositionPoint | sequenceNumber | Zero-relative sequence number of this point within a series of points. | GL | 1..0 | .sequenceNumber not required if there is only one PositionPoint associated with Location If there are multiple PositionPoints associated with Location, .sequenceNumber shall start with 1 and shall increment by one across PositionPoints. |  |  | Geographical 0..1 | yes
YES | PositionPoint | xPosition | X axis position. | GL | 1..1 |  |  |  | Geographical 1..1 | yes
YES | PositionPoint | yPosition | Y axis position. | GL | 1..1 |  |  |  | Geographical 1..1 | yes
OPTIONAL | PositionPoint | zPosition | (if applicable) Z axis position. | GL | 0..1 |  |  |  | Geographical 0..1 | yes

## DL - Diagram Layout
Class | Parent Class or Class | Attribute | Description (CIM Notes) | LTDS Profile | LTDS UML Constraint | LTDS Additional Constraints | Change from CGMES 3.0 | In CGMES 3.0 profile | In 61970-453 Ed 2 plus Ed 2.1 profile | In CIM information model | Comments / Questions | Existing LTDS requirement | Proposed GC0139 requirement
Instance Requirements |  |  | General Philosophy for containment: ss Mandatory A GSPSchematic diagram layout for each GSP displaying - Substation name - Line name - ConductingEquipment (including load and generation) symbol - ConductingEquipment name for PowerTransformer, BusbarSection - BusbarSection VoltageLevel name - Switch normal open / normal closed A SubstationSchematic diagramlayout for each Substation (or group of Primary Substations) displaying - Substation name - Line name - ConductingEquipment (including load and generation)symbol - ConductingEquipment name for PowerTransformer, BusbarSection, Switches, significant load and generation - BusbarSection VoltageLevel name - Switch normal open / normal closed A GSPGeographic diagram layout for each GSP displaying ... - Substation name and boundary, if defined - Line name - ConductingEquipment (including load and generation) symbol - ConductingEquipment name for PowerTransformer, BusbarSection - BusbarSection VoltageLevel name - Switch normal open / normal closed A LicenceRegionGeographic diagram layout for each GSP displaying... - Substation symbol and name - Line symbol Allowed - Additional diagram layouts to aid in understanding - Use of VisibilityLayer to improve user experience |  |  |  | none |  |  |  | Change to format but not content of existing LTDS: - significant increase in specificity of diagram requirement - same general level of content required for schematic and geographic plans | p 5 "The approximate locations of 132kV and EHV circuits and substations are shown on geographic plan(s) of sufficient scale to allow a user to identify if there is network at these voltage levels in an area." p 6 "Schematic diagrams shall be provided of sufficient scale and clarity to assist a user in interpreting and using the detailed network information." p 6 "Normal open points shall be clearly indicated on all schematic diagrams" p 7 "TABLE 1 - CIRCUIT DATA ...Data should be clearly linked with ... network schematic diagrams" p 8 "TABLE 2 - TRANSFORMER DATA ...Data should be clearly linked with ... network schematic diagrams" p 9 "TABLE 3 - LOAD INFORMATION ...Data should be clearly linked with network schematic diagrams" p 10 "TABLE 4 - FAULT LEVEL INFORMATION ...Data should be clearly linked with network schematic diagrams" p 11 "TABLE 5 - GENERATION ...Nomenclature used for substation names shall clearly align with that on the schematic diagrams." p 13 "TABLE 6 - TABLE OF INTEREST IN A CONNECTION ...Nomenclature used for substation names shall clearly align with that on the schematic diagrams."
Unsatisfied requirements
IdentifiedObject
| IdentifiedObject This is a root class to provide common identification for all classes needing identification and naming attributes. |  |  | DL |  |  |  |  | DL | yes
| IdentifiedObject | aliasName | The aliasName is free text human readable name of the object alternative to IdentifiedObject.name. It may be non unique and may not correlate to a naming hierarchy. The attribute aliasName is retained because of backwards compatibility between CIM releases. It is however recommended to replace aliasName with the Name class as aliasName is planned for retirement at a future time. | none |  |  |  | none | DL 0..1 | yes
| IdentifiedObject | description | The description is a free human readable text describing or naming the object. It may be non unique and may not correlate to a naming hierarchy. | DL | 0..1 |  |  | DL 0..1 | DL 0..1 | yes
| IdentifiedObject | mRID | Master resource identifier issued by a model authority. The mRID is unique within an exchange context. Global uniqueness is easily achieved by using a UUID, as specified in IETF RFC 4122, for the mRID. The use of UUID is strongly recommended. For CIMXML data files in RDF syntax conforming to IEC 61970-552, the mRID is mapped to rdf:ID or rdf:about attributes that identify CIM object elements. | DL | 1..1 |  |  | DL 1..1 | DL 0..1 | yes | mRID does appear to be optional in the CDV of 61970-453 Ed2.1
| IdentifiedObject | name | The name is any free human readable and possibly non unique text naming the object. | DL | 1..1 |  |  | DL 1..1 | DL 0..1 | yes
Diagram
IdentifiedObject
| IdentifiedObject | aliasName |  | none | 0
| IdentifiedObject | description |  | DL | 0..1
| IdentifiedObject | mRID |  | DL | 1..1
| IdentifiedObject | name |  | DL | 1..1
| Diagram The diagram being exchanged. The coordinate system is a standard Cartesian coordinate system and the orientation attribute defines the orientation. The initial view related attributes can be used to specify an initial view with the x,y coordinates of the diagonal points. |  |  | DL |  |  |  |  | DL | yes
| Diagram | orientation | The Diagram represents the diagram being exchanged. The initialView attributes can be used to specify an initial view with the x,y coordinates of the diagonal points. The coordinate system is a standard Cartesian coordinate system and the orientation attribute defines a positive or negative orientation. | DL | 1..1 |  |  | DL 1..1 | DL 0..1 | yes
| Diagram | x1InitialView | X coordinate of the first corner of the initial view | DL | 0..1 |  |  | DL 0..1 | DL 0..1 | yes
| Diagram | x2InitialView | X coordinate of the second corner of the initial view | DL | 0..1 |  |  | DL 0..1 | DL 0..1 | yes
| Diagram | y1InitialView | Y coordinate of the first corner of the initial view | DL | 0..1 |  |  | DL 0..1 | DL 0..1 | yes
| Diagram | y2InitialView | Y coordinate of the second corner of the initial view | DL | 0..1 |  |  | DL 0..1 | DL 0..1 | yes
DiagramStyle
IdentifiedObject
| IdentifiedObject | aliasName |  | none | 0
| IdentifiedObject | description |  | DL | 0..1
| IdentifiedObject | mRID |  | DL | 1..1
| IdentifiedObject | name |  | DL | 1..1 | [5 empty] | what is Alan's tool putting out as options? I would think something like: - GSPSchematic - SubstationSchematic - GSPGeographic - LicenceRegionGeographic
| DiagramStyle The diagram style refers to a style used by the originating system for a diagram. A diagram style describes information such as schematic, geographic, etc. |  |  | DL |  |  |  |  | DL | yes
DiagramObject
IdentifiedObject
| IdentifiedObject | aliasName |  | none | 0
| IdentifiedObject | description |  | DL | 0..1
| IdentifiedObject | mRID |  | DL | 1..1
| IdentifiedObject | name |  | DL | 1..1
| DiagramObject An object that defines one or more points in a given space. This object can be associated with anything that specializes IdentifiedObject. For single line diagrams such objects typically include such items as analog values, breakers, disconnectors, power transformers, and transmission lines. |  |  | DL |  |  |  |  | DL | yes
| DiagramObject | drawingOrder | The drawing order of this element. The higher the number, the later the element is drawn in sequence. This is used to ensure that elements that overlap are rendered in the correct order. | DL | 0..1 |  |  | DL 0..1 | DL 0..1 | yes
| DiagramObject | isPolygon | Defines whether or not the diagram objects points define the boundaries of a polygon or the routing of a polyline. If this value is true then a receiving application should consider the first and last points to be connected. | DL | 0..1 |  |  | DL 0..1 | DL 0..1 | yes
| DiagramObject | offsetX | The offset in the X direction. This is used for defining the offset from centre for rendering an icon (the default is that a single point specifies the centre of the icon). The offset is in per-unit with 0 indicating there is no offset from the horizontal centre of the icon. - 0,5 indicates it is offset by 50 % to the left and 0,5 indicates an offset of 50 % to the right. | DL | 0..1 |  |  | DL 0..1 | DL 0..1 | yes
| DiagramObject | offsetY | The offset in the Y direction. This is used for defining the offset from centre for rendering an icon (the default is that a single point specifies the centre of the icon). The offset is in per-unit with 0 indicating there is no offset from the vertical centre of the icon. The offset direction is dependent on the orientation of the diagram, with -0,5 and 0,5 indicating an offset of ± 50 % on the vertical axis. | DL | 0..1 |  |  | DL 0..1 | DL 0..1 | yes
| DiagramObject | rotation | Sets the angle of rotation (in Degrees) of the diagram object in a clockwise direction from the normal | DL | 0..1 |  |  | DL 0..1 | DL 0..1 | yes
TextDiagramObject
IdentifiedObject
| IdentifiedObject | aliasName |  | none | 0
| IdentifiedObject | description |  | DL | 0..1
| IdentifiedObject | mRID |  | DL | 1..1
| IdentifiedObject | name |  | DL | 1..1
DiagramObject
| DiagramObject | drawingOrder |  | DL | 0..1
| DiagramObject | isPolygon |  | DL | 0..1
| DiagramObject | offsetX |  | DL | 0..1
| DiagramObject | offsetY |  | DL | 0..1
| DiagramObject | rotation |  | DL | 0..1
| TextDiagramObject A diagram object for placing free-text or text derived from an associated domain object. |  |  | DL |  |  |  |  | DL | yes
| TextDiagramObject | text | The text that is displayed by this text diagram object. | DL | 0..1 |  |  | DL 0..1 | DL 0..1 | yes
VisibilityLayer
IdentifiedObject
| IdentifiedObject | aliasName |  | none | 0
| IdentifiedObject | description |  | DL | 0..1
| IdentifiedObject | mRID |  | DL | 1..1
| IdentifiedObject | name |  | DL | 1..1
| VisibilityLayer Layers are typically used for grouping diagram objects according to themes and scales. Themes are used to display or hide certain information (e.g., lakes, borders), while scales are used for hiding or displaying information depending on the current zoom level (hide text when it is too small to be read, or when it exceeds the screen size). This is also called de-cluttering. The diagram layout profile will support an m:n relationship between diagram objects and layers. It will be the task of the importing system to convert an m:n case into an appropriate 1:n representation if the importing system does not support m:n. |  |  | DL |  |  |  |  | DL | yes
| VisibilityLayer | drawingOrder | The drawing order for this layer. As with the drawingOrder for diagram objects, the higher the number, the later the layer and the objects within it are rendered. | DL | 0..1 |  |  | DL 0..1 | DL 0..1 | yes
DiagramObjectStyle
IdentifiedObject
| IdentifiedObject | aliasName |  | none | 0
| IdentifiedObject | description |  | DL | 0..1
| IdentifiedObject | mRID |  | DL | 1..1
| IdentifiedObject | name |  | DL | 1..1
| DiagramObjectStyle A reference to a style used by the originating system for a diagram object. A diagram object style describes information such as line thickness, shape such as circle or rectangle etc, and colour. |  |  | DL |  |  |  |  | DL | yes | Any reason for multiple styles?
DiagramObjectPoint
| DiagramObjectPoint A point in a given space defined by 3 coordinates and associated to a diagram object. The coordinates may be positive or negative as the origin does not have to be in the corner of a diagram. |  |  | DL |  |  |  |  | DL | yes
| DiagramObjectPoint | sequenceNumber | The sequence position of the point, used for defining the order of points for DiagramObjects acting as a polyline or polygon with more than one point | DL | 0..1 |  |  | DL 0..1 | DL 0..1 | yes
| DiagramObjectPoint | xPosition | The X coordinate of this point | DL | 1..1 |  |  | DL 1..1 | DL 1..1 | yes
| DiagramObjectPoint | yPosition | The Y coordinate of this point | DL | 1..1 |  |  | DL 1..1 | DL 1..1 | yes
| DiagramObjectPoint | zPosition | The Z coordinate of this point | DL | 0..1 |  |  | DL 0..1 | DL 0..1 | yes
DiagramObjectGluePoint
| DiagramObjectGluePoint This is used for grouping diagram object points from different diagram objects that are considered to be glued together in a diagram even if they are not at the exact same coordinates. |  |  | DL |  |  |  |  | DL | yes

## EQ SC SSH - EnergyConnection
Class | Parent Class or Class | Attribute | Description (CIM Notes) | LTDS Profile | LTDS UML Constraint | LTDS Additional Constraints | In CGMES 3.0 profile | In 61970-452 Ed4 EQ, SC, OP or 61970-456 Ed3 SSH profiles | In CIM information model | Comments / Questions | Existing LTDS requirement | Proposed GC0139 requirement
EnergyConnection
IdentifiedObject
| IdentifiedObject | aliasName
| IdentifiedObject | description
| IdentifiedObject | mRID
| IdentifiedObject | name
PowerSystemResource
Equipment
| Equipment | aggregate
| Equipment | inService
| Equipment | networkAnalysisEnabled
| Equipment | normallyInService
ConductingEquipment
| EnergyConnection A connection of energy generation or consumption on the power system model. | [6 empty] | EQ, SC, SSH | yes
EnergyConsumer
IdentifiedObject
| IdentifiedObject | aliasName
| IdentifiedObject | description
| IdentifiedObject | mRID
| IdentifiedObject | name
PowerSystemResource
Equipment
| Equipment | aggregate
| Equipment | inService
| Equipment | networkAnalysisEnabled
| Equipment | normallyInService
ConductingEquipment
EnergyConnection
| EnergyConsumer Generic user of energy - a point of consumption on the power system model. EnergyConsumer.pfixed, .qfixed, .pfixedPct and .qfixedPct have meaning only if there is no LoadResponseCharacteristic associated with EnergyConsumer or if LoadResponseCharacteristic.exponentModel is set to False. | [6 empty] | EQ, SSH | yes
| EnergyConsumer | customerCount | Number of individual customers represented by this demand. | Basic | 0..1 FROM GMDM |  |  | none | yes
| EnergyConsumer | grounded | Used for Yn and Zn connections. True if the neutral is solidly grounded. | Basic | 0..1 required if phaseConnection=Yn or I, else no attribute |  |  | none | yes
| EnergyConsumer | p | Active power of the load. Load sign convention is used, i.e. positive sign means flow out from a node. For voltage dependent loads the value is at rated voltage. Starting value for a steady state solution. | SSH | 1..1 shall equal the sum of .p of associated EnergyConsumerPhase if any exist |  |  | SSH 0..1 | yes
| EnergyConsumer | pfixed | Active power of the load that is a fixed quantity and does not vary as load group value varies. Load sign convention is used, i.e. positive sign means flow out from a node. | none (Basic) | <NOTE: using EnergyConsumerPhase attribute instead> |  |  | EQ 0..1 | yes
| EnergyConsumer | pfixedPct | Fixed active power as a percentage of load group fixed active power. Used to represent the time-varying components. Load sign convention is used, i.e. positive sign means flow out from a node. | none (Basic) | <NOTE: using EnergyConsumerPhase attribute instead> |  |  | EQ 0..1 | yes
| EnergyConsumer | phaseConnection | The type of phase connection, such as wye or delta. | Basic | 1..1 |  |  | none | yes
| EnergyConsumer | q | Reactive power of the load. Load sign convention is used, i.e. positive sign means flow out from a node. For voltage dependent loads the value is at rated voltage. Starting value for a steady state solution. | SSH | 1..1 shall equal the sum of .q of associated EnergyConsumerPhase if any exist |  |  | SSH 0..1 | yes
| EnergyConsumer | qfixed | Reactive power of the load that is a fixed quantity and does not vary as load group value varies. Load sign convention is used, i.e. positive sign means flow out from a node. | none (Basic) | <NOTE: using EnergyConsumerPhase attribute instead> |  |  | EQ 0..1 | yes
| EnergyConsumer | qfixedPct | Fixed reactive power as a percentage of load group fixed reactive power. Used to represent the time-varying components. Load sign convention is used, i.e. positive sign means flow out from a node. | none (Basic) | <NOTE: using EnergyConsumerPhase attribute instead> |  |  | EQ 0..1 | yes
EnergySource
IdentifiedObject
| IdentifiedObject | aliasName
| IdentifiedObject | description
| IdentifiedObject | mRID
| IdentifiedObject | name
PowerSystemResource
Equipment
| Equipment | aggregate
| Equipment | inService
| Equipment | networkAnalysisEnabled
| Equipment | normallyInService
ConductingEquipment
EnergyConnection
| EnergySource A generic equivalent for an energy supplier on a transmission or distribution voltage level. | [6 empty] | EQ, SC, SSH | yes
| EnergySource | activePower | High voltage source active injection. Load sign convention is used, i.e. positive sign means flow out from a node. Starting value for steady state solutions. | none (SSH) | FROM GMDM |  |  | SSH 1..1 | yes
| EnergySource | nominalVoltage | Phase-to-phase nominal voltage. | Basic | 0..1 |  |  | EQ 0..1 | yes
| EnergySource | pMax | This is the maximum active power that can be produced by the source. Load sign convention is used, i.e. positive sign means flow out from a TopologicalNode (bus) into the conducting equipment. | none (Basic) |  |  |  | EQ 0..1 | yes
| EnergySource | pMin | This is the minimum active power that can be produced by the source. Load sign convention is used, i.e. positive sign means flow out from a TopologicalNode (bus) into the conducting equipment. | none (Basic) |  |  |  | EQ 0..1 | yes
| EnergySource | r | Positive sequence Thevenin resistance. | Basic | 1..1 |  |  | SC 0..1 | yes
| EnergySource | r0 | Zero sequence Thevenin resistance. | Basic | 1..1 |  |  | SC 0..1 | yes
| EnergySource | reactivePower | High voltage source reactive injection. Load sign convention is used, i.e. positive sign means flow out from a node. Starting value for steady state solutions. | none (SSH) |  |  |  | SSH 1..1 | yes
| EnergySource | rn | Negative sequence Thevenin resistance. | none (Basic) |  |  |  | SC 0..1 | yes
| EnergySource | voltageAngle | Phase angle of a-phase open circuit used when voltage characteristics need to be imposed at the node associated with the terminal of the energy source, such as when voltages and angles from the transmission level are used as input to the distribution network. The attribute shall be a positive value or zero. | SSH | 0..1 shall be zero or positive |  |  | SSH 0..1 | yes
| EnergySource | voltageMagnitude | Phase-to-phase open circuit voltage magnitude used when voltage characteristics need to be imposed at the node associated with the terminal of the energy source, such as when voltages and angles from the transmission level are used as input to the distribution network. The attribute shall be a positive value or zero. | SSH | 0..1 shall be zero or positive |  |  | SSH 0..1 | yes
| EnergySource | x | Positive sequence Thevenin reactance. | Basic | 1..1 |  |  | SC 0..1 | yes
| EnergySource | x0 | Zero sequence Thevenin reactance. | Basic | 1..1 |  |  | SC 0..1 | yes
| EnergySource | xn | Negative sequence Thevenin reactance. | none (Basic) |  |  |  | SC 0..1 | yes
RegulatingCondEq
IdentifiedObject
| IdentifiedObject | aliasName
| IdentifiedObject | description
| IdentifiedObject | mRID
| IdentifiedObject | name
PowerSystemResource
Equipment
| Equipment | aggregate
| Equipment | inService
| Equipment | networkAnalysisEnabled
| Equipment | normallyInService
ConductingEquipment
EnergyConnection
| RegulatingCondEq A type of conducting equipment that can regulate a quantity (i.e. voltage or flow) at a specific point in the network. | [6 empty] | EQ, SC, SSH | yes
| RegulatingCondEq | controlEnabled | Specifies the regulation status of the equipment. True is regulating, false is not regulating. | SSH | 1..1 |  |  | SSH 1..1 | yes

## XX EnergyConsumer EnergySource
Class | Parent Class or Class | Attribute | Description (CIM Notes) | LTDS Profile | LTDS UML Constraint | LTDS Additional Constraints | In CGMES profile | In 61970-45x profile | In CIM information model | Comments / Questions | Existing LTDS requirement | Proposed GC0139 requirement
EnergyConsumer
IdentifiedObject
| IdentifiedObject | description |  | Basic | 1..1
| IdentifiedObject | name |  | Basic | 1..1
PowerSystemResource
Equipment
| Equipment | inService | Specifies the availability of the equipment. True means the equipment is available for topology processing, which determines if the equipment is energized or not. False means that the equipment is treated by network applications as if it is not in the model. | SSH | 0..1 required (and =false) if equipment not in service, else no attribute
ConductingEquipment
EnergyConnection A connection of energy generation or consumption on the power system model.
EnergyConsumer Generic user of energy - a point of consumption on the power system model. EnergyConsumer.pfixed, .qfixed, .pfixedPct and .qfixedPct have meaning only if there is no LoadResponseCharacteristic associated with EnergyConsumer or if LoadResponseCharacteristic.exponentModel is set to False.
| EnergyConsumer | customerCount | Number of individual customers represented by this demand. | Basic | 0..1
| EnergyConsumer | grounded | Used for Yn and Zn connections. True if the neutral is solidly grounded. | Basic | 0..1 required if phaseConnection=Yn or I, else no attribute
| EnergyConsumer | p | Active power of the load. Load sign convention is used, i.e. positive sign means flow out from a node. For voltage dependent loads the value is at rated voltage. Starting value for a steady state solution. | SSH | 1..1 shall equal the sum of .p of associated EnergyConsumerPhase if any exist
| EnergyConsumer | pfixed | Active power of the load that is a fixed quantity and does not vary as load group value varies. Load sign convention is used, i.e. positive sign means flow out from a node. | none (Basic) | <NOTE: using EnergyConsumerPhase attribute instead>
| EnergyConsumer | pfixedPct | Fixed active power as a percentage of load group fixed active power. Used to represent the time-varying components. Load sign convention is used, i.e. positive sign means flow out from a node. | none (Basic) | <NOTE: using EnergyConsumerPhase attribute instead>
| EnergyConsumer | phaseConnection | The type of phase connection, such as wye or delta. | Basic | 1..1
| EnergyConsumer | q | Reactive power of the load. Load sign convention is used, i.e. positive sign means flow out from a node. For voltage dependent loads the value is at rated voltage. Starting value for a steady state solution. | SSH | 1..1 shall equal the sum of .q of associated EnergyConsumerPhase if any exist
| EnergyConsumer | qfixed | Reactive power of the load that is a fixed quantity and does not vary as load group value varies. Load sign convention is used, i.e. positive sign means flow out from a node. | none (Basic) | <NOTE: using EnergyConsumerPhase attribute instead>
| EnergyConsumer | qfixedPct | Fixed reactive power as a percentage of load group fixed reactive power. Used to represent the time-varying components. Load sign convention is used, i.e. positive sign means flow out from a node. | none (Basic) | <NOTE: using EnergyConsumerPhase attribute instead>
EnergyConsumerPhase
IdentifiedObject
| IdentifiedObject | description |  | Basic | 0..1
| IdentifiedObject | name |  | Basic | 1..1
PowerSystemResource
EnergyConsumerPhase A single phase of an energy consumer.
| EnergyConsumerPhase | p | Active power of the load. Load sign convention is used, i.e. positive sign means flow out from a node. For voltage dependent loads the value is at rated voltage. Starting value for a steady state solution. | SSH | 1..1
| EnergyConsumerPhase | pfixed | Active power of the load that is a fixed quantity. Load sign convention is used, i.e. positive sign means flow out from a node. | none (Basic)
| EnergyConsumerPhase | pfixedPct | Fixed active power as per cent of load group fixed active power. Load sign convention is used, i.e. positive sign means flow out from a node. | none (Basic)
| EnergyConsumerPhase | phase | Phase of this energy consumer component. If the energy consumer is wye connected, the connection is from the indicated phase to the central ground or neutral point. If the energy consumer is delta connected, the phase indicates an energy consumer connected from the indicated phase to the next logical non-neutral phase. | Basic | 1..1
| EnergyConsumerPhase | q | Reactive power of the load. Load sign convention is used, i.e. positive sign means flow out from a node. For voltage dependent loads the value is at rated voltage. Starting value for a steady state solution. | SSH | 1..1
| EnergyConsumerPhase | qfixed | Reactive power of the load that is a fixed quantity. Load sign convention is used, i.e. positive sign means flow out from a node. | none (Basic)
| EnergyConsumerPhase | qfixedPct | Fixed reactive power as per cent of load group fixed reactive power. Load sign convention is used, i.e. positive sign means flow out from a node. | none (Basic)
LoadResponseCharacteristic
IdentifiedObject
| IdentifiedObject | description |  | Basic | 0..1
| IdentifiedObject | name |  | Basic | 1..1
LoadResponseCharacteristic Models the characteristic response of the load demand due to changes in system conditions such as voltage and frequency. It is not related to demand response. If LoadResponseCharacteristic.exponentModel is True, the exponential voltage or frequency dependent models are specified and used as to calculate active and reactive power components of the load model. The equations to calculate active and reactive power components of the load model are internal to the power flow calculation, hence they use different quantities depending on the use case of the data exchange. The equations for exponential voltage dependent load model injected power are: pInjection= Pnominal* (Voltage/cim:BaseVoltage.nominalVoltage) ** cim:LoadResponseCharacteristic.pVoltageExponent qInjection= Qnominal* (Voltage/cim:BaseVoltage.nominalVoltage) ** cim:LoadResponseCharacteristic.qVoltageExponent Where: 1) * means "multiply" and ** is "raised to the power of"; 2) Pnominal and Qnominal represent the active power and reactive power at nominal voltage as any load described by the voltage exponential model shall be given at nominal voltage. This means that EnergyConsumer.p and EnergyConsumer.q are at nominal voltage. 3) After power flow is solved: -pInjection and qInjection correspond to SvPowerflow.p and SvPowerflow.q respectively. - Voltage corresponds to SvVoltage.v at the TopologicalNode where the load is connected.
| LoadResponseCharacteristic | exponentModel | Indicates the exponential voltage dependency model is to be used. If false, the coefficient model is to be used. The exponential voltage dependency model consist of the attributes: - pVoltageExponent - qVoltageExponent - pFrequencyExponent - qFrequencyExponent. The coefficient model consist of the attributes: - pConstantImpedance - pConstantCurrent - pConstantPower - qConstantImpedance - qConstantCurrent - qConstantPower. The sum of pConstantImpedance, pConstantCurrent and pConstantPower shall equal 1. The sum of qConstantImpedance, qConstantCurrent and qConstantPower shall equal 1. | Basic | 1..1 =false
| LoadResponseCharacteristic | pConstantCurrent | Portion of active power load modelled as constant current. | Basic | 1..1 sum of pConstantImpedance, pConstantCurrent and pConstantPower shall equal 1
| LoadResponseCharacteristic | pConstantImpedance | Portion of active power load modelled as constant impedance. | Basic | 1..1 sum of pConstantImpedance, pConstantCurrent and pConstantPower shall equal 1
| LoadResponseCharacteristic | pConstantPower | Portion of active power load modelled as constant power. | Basic | 1..1 sum of pConstantImpedance, pConstantCurrent and pConstantPower shall equal 1
| LoadResponseCharacteristic | pFrequencyExponent | Exponent of per unit frequency effecting active power. | none (Basic)
| LoadResponseCharacteristic | pVoltageExponent | Exponent of per unit voltage effecting real power. | none (Basic)
| LoadResponseCharacteristic | qConstantCurrent | Portion of reactive power load modelled as constant current. | Basic | 1..1 sum of qConstantImpedance, qConstantCurrent and qConstantPower shall equal 1
| LoadResponseCharacteristic | qConstantImpedance | Portion of reactive power load modelled as constant impedance. | Basic | 1..1 sum of qConstantImpedance, qConstantCurrent and qConstantPower shall equal 1
| LoadResponseCharacteristic | qConstantPower | Portion of reactive power load modelled as constant power. | Basic | 1..1 sum of qConstantImpedance, qConstantCurrent and qConstantPower shall equal 1
| LoadResponseCharacteristic | qFrequencyExponent | Exponent of per unit frequency effecting reactive power. | none (Basic)
| LoadResponseCharacteristic | qVoltageExponent | Exponent of per unit voltage effecting reactive power. | none (Basic)
PointOfCommonCoupling |  |  |  |  | in the GMDM IOP, every distinct entity to which operating responsibility changes (aka every 'customer') is assumed to have a PointOfCommonCoupling (even though customer is not modeled in the test model) | Yes
IdentifiedObject
| IdentifiedObject | description |  | Basic | 0..1
| IdentifiedObject | name |  | Basic | 1..1
| PointOfCommonCoupling A grid location (Terminal) at which grid operational responsibility changes. It is a grid location that often has associated with it: • Identity or contact information of entity with operating responsibility • Measured quantities or states (most common of which is power exchange) • Contractual commitments (for P, Q, V services) • A point at which (in analysis) facilities on the other side are regulating some quantity |  |  |  |  | yes
EnergySource
IdentifiedObject
| IdentifiedObject | description |  | Basic | 1..1
| IdentifiedObject | name |  | Basic | 1..1
PowerSystemResource
Equipment
| Equipment | inService | Specifies the availability of the equipment. True means the equipment is available for topology processing, which determines if the equipment is energized or not. False means that the equipment is treated by network applications as if it is not in the model. | SSH | 0..1 required (and =false) if equipment not in service, else no attribute
ConductingEquipment
EnergyConnection A connection of energy generation or consumption on the power system model.
EnergySource A generic equivalent for an energy supplier on a transmission or distribution voltage level.
| EnergySource | activePower | High voltage source active injection. Load sign convention is used, i.e. positive sign means flow out from a node. Starting value for steady state solutions. | none (SSH)
| EnergySource | nominalVoltage | Phase-to-phase nominal voltage. | Basic | 0..1
| EnergySource | pMax | This is the maximum active power that can be produced by the source. Load sign convention is used, i.e. positive sign means flow out from a TopologicalNode (bus) into the conducting equipment. | none (Basic)
| EnergySource | pMin | This is the minimum active power that can be produced by the source. Load sign convention is used, i.e. positive sign means flow out from a TopologicalNode (bus) into the conducting equipment. | none (Basic)
| EnergySource | r | Positive sequence Thevenin resistance. | Basic | 1..1
| EnergySource | r0 | Zero sequence Thevenin resistance. | Basic | 1..1
| EnergySource | reactivePower | High voltage source reactive injection. Load sign convention is used, i.e. positive sign means flow out from a node. Starting value for steady state solutions. | none (SSH)
| EnergySource | rn | Negative sequence Thevenin resistance. | none (Basic)
| EnergySource | voltageAngle | Phase angle of a-phase open circuit used when voltage characteristics need to be imposed at the node associated with the terminal of the energy source, such as when voltages and angles from the transmission level are used as input to the distribution network. The attribute shall be a positive value or zero. | SSH | 0..1 shall be zero or positive
| EnergySource | voltageMagnitude | Phase-to-phase open circuit voltage magnitude used when voltage characteristics need to be imposed at the node associated with the terminal of the energy source, such as when voltages and angles from the transmission level are used as input to the distribution network. The attribute shall be a positive value or zero. | SSH | 0..1 shall be zero or positive
| EnergySource | x | Positive sequence Thevenin reactance. | Basic | 1..1
| EnergySource | x0 | Zero sequence Thevenin reactance. | Basic | 1..1
| EnergySource | xn | Negative sequence Thevenin reactance. | none (Basic)

## XX PowerElectronicsConnnection
Class | Parent Class or Class | Attribute | Description (CIM Notes) | LTDS Profile | LTDS UML Constraint | LTDS Additional Constraints | In CGMES profile | In 61970-45x profile | In CIM information model | Existing LTDS requirement | Proposed GC0139 requirement
PowerElectronicsConnection | [10 empty] | For < 1MW Small Power Stations Total MW aggregated by generation type at the 'Connected Node' (which is a BSP, apparently)
| IdentifiedObject | [9 empty] | For > or = 1MW at the Connected Node (aka BSP.. hmm, if a generator is on 11 kV then will appear at the low side of a 33 to 11 kV xf, otherwise it will appear at its actual grid location, which, at least for generation on the 132kV network might be at a location fed by multiple BSPs) individual information like fuel type, if part of combined heat & power, capacity, control mode & details if voltage control, loss of mains protection info, add'l info if storage
| IdentifiedObject | description |  | Basic | 1..1 | [5 empty] | if generator is - 'large' or - 'medium' and connected to the first voltage leve below the transmission voltage then Data Registration Code (DRC) data must be provided. Note that size is location-dependent - see table at R.
| IdentifiedObject | name |  | Basic | 1..1
PowerSystemResource
Equipment
| Equipment | inService | Specifies the availability of the equipment. True means the equipment is available for topology processing, which determines if the equipment is energized or not. False means that the equipment is treated by network applications as if it is not in the model. | SSH | 0..1 required (and =false) if equipment not in service, else no attribute
ConductingEquipment
EnergyConnection A connection of energy generation or consumption on the power system model.
RegulatingCondEq A type of conducting equipment that can regulate a quantity (i.e. voltage or flow) at a specific point in the network.
| RegulatingCondEq | controlEnabled | Specifies the regulation status of the equipment. True is regulating, false is not regulating. | SSH | 1..1
PowerElectronicsConnection A connection to the AC network for energy production or consumption that uses power electronics rather than rotating machines.
| PowerElectronicsConnection | maxIFault | Maximum fault current this device will contribute, in per-unit of rated current, before the converter protection will trip or bypass. | Basic | 1..1
| PowerElectronicsConnection | maxQ | Maximum reactive power limit. This is the maximum (nameplate) limit for the unit. | Basic | 1..1
| PowerElectronicsConnection | minQ | Minimum reactive power limit for the unit. This is the minimum (nameplate) limit for the unit. | Basic | 1..1
| PowerElectronicsConnection | p | Active power injection. Load sign convention is used, i.e. positive sign means flow out from a node. Starting value for a steady state solution. | SSH | 1..1 shall equal the sum of .p of associated PowerElectronicsConnectionPhase if any exist
| PowerElectronicsConnection | q | Reactive power injection. Load sign convention is used, i.e. positive sign means flow out from a node. Starting value for a steady state solution. | SSH | 1..1 shall equal the sum of .q of associated PowerElectronicsConnectionPhase if any exist
| PowerElectronicsConnection | ratedS | Nameplate apparent power rating for the unit. The attribute shall have a positive value. | Basic | 1..1 shall be positive should be approximately equal to the sum of all associated PowerElectronicsUnit.maxP
| PowerElectronicsConnection | ratedU | Rated voltage (nameplate data, Ur in IEC 60909-0). It is primarily used for short circuit data exchange according to IEC 60909. The attribute shall be a positive value. | Basic | 0..1 shall be positive
PowerElectronicsConnectionPhase
IdentifiedObject
| IdentifiedObject | description |  | Basic | 0..1
| IdentifiedObject | name |  | Basic | 1..1
PowerSystemResource
PowerElectronicsConnectionPhase A single phase of a power electronics connection.
| PowerElectronicsConnectionPhase | p | Active power injection. Load sign convention is used, i.e. positive sign means flow into the equipment from the network. | SSH | 1..1
| PowerElectronicsConnectionPhase | phase | Phase of this energy producer component. If the energy producer is wye connected, the connection is from the indicated phase to the central ground or neutral point. If the energy producer is delta connected, the phase indicates an energy producer connected from the indicated phase to the next logical non-neutral phase. | Basic | 1..1
| PowerElectronicsConnectionPhase | q | Reactive power injection. Load sign convention is used, i.e. positive sign means flow into the equipment from the network. | SSH | 1..1
BatteryUnit
IdentifiedObject
| IdentifiedObject | description |  | Basic | 0..1
| IdentifiedObject | name |  | Basic | 1..1
PowerSystemResource
Equipment
| Equipment | inService | Specifies the availability of the equipment. True means the equipment is available for topology processing, which determines if the equipment is energized or not. False means that the equipment is treated by network applications as if it is not in the model. | SSH | 0..1 required (and =false) if equipment not in service, else no attribute
PowerElectronicsUnit A generating unit or battery or aggregation that connects to the AC network using power electronics rather than rotating machines.
| PowerElectronicsUnit | maxP | Maximum active power limit. This is the maximum (nameplate) limit for the unit. | Basic | 1..1
| PowerElectronicsUnit | minP | Minimum active power limit. This is the minimum (nameplate) limit for the unit. | Basic | 1..1
BatteryUnit An electrochemical energy storage device.
| BatteryUnit | batteryState | The current state of the battery (charging, full, etc.). | SSH | 1..1
| BatteryUnit | ratedE | Full energy storage capacity of the battery. The attribute shall be a positive value. | Basic | 1..1 shall be positive
| BatteryUnit | storedE | Amount of energy currently stored. The attribute shall be a positive value or zero and lower than BatteryUnit.ratedE. | SSH | 1..1 shall be zero or positive and less than ratedE
PhotoVoltaicUnit
IdentifiedObject
| IdentifiedObject | description |  | Basic | 0..1
| IdentifiedObject | name |  | Basic | 1..1
PowerSystemResource
Equipment
| Equipment | inService | Specifies the availability of the equipment. True means the equipment is available for topology processing, which determines if the equipment is energized or not. False means that the equipment is treated by network applications as if it is not in the model. | SSH | 0..1 required (and =false) if equipment not in service, else no attribute
PowerElectronicsUnit A generating unit or battery or aggregation that connects to the AC network using power electronics rather than rotating machines.
| PowerElectronicsUnit | maxP | Maximum active power limit. This is the maximum (nameplate) limit for the unit. | Basic | 1..1
| PowerElectronicsUnit | minP | Minimum active power limit. This is the minimum (nameplate) limit for the unit. | Basic | 1..1
PhotoVoltaicUnit A photovoltaic device or an aggregation of such devices.
PowerElectronicsWindUnit
IdentifiedObject
| IdentifiedObject | description |  | Basic | 0..1
| IdentifiedObject | name |  | Basic | 1..1
PowerSystemResource
Equipment
| Equipment | inService | Specifies the availability of the equipment. True means the equipment is available for topology processing, which determines if the equipment is energized or not. False means that the equipment is treated by network applications as if it is not in the model. | SSH | 0..1 required (and =false) if equipment not in service, else no attribute
PowerElectronicsUnit A generating unit or battery or aggregation that connects to the AC network using power electronics rather than rotating machines.
| PowerElectronicsUnit | maxP | Maximum active power limit. This is the maximum (nameplate) limit for the unit. | Basic | 1..1
| PowerElectronicsUnit | minP | Minimum active power limit. This is the minimum (nameplate) limit for the unit. | Basic | 1..1
PowerElectronicsWindUnit A wind generating unit that connects to the AC network with power electronics rather than rotating machines or an aggregation of such units.

## EQ SC SSH - Other CondEquip
Class | Parent Class or Class | Attribute | Description (CIM Notes) | LTDS Profile | LTDS UML Constraint | LTDS Additional Constraints | In CGMES 3.0 profile | In 61970-452 Ed4 EQ, SC, OP or 61970-456 Ed3 SSH profiles | In CIM information model | Comments / Questions | Existing LTDS requirement | Proposed GC0139 requirement
Connector
Junction
BusBarSection
IdentifiedObject
| IdentifiedObject | description |  | Basic | 1..1 | 1..1
| IdentifiedObject | name |  | Basic | 1..1 | 1..1
PowerSystemResource
Equipment
| Equipment | inService | Specifies the availability of the equipment. True means the equipment is available for topology processing, which determines if the equipment is energized or not. False means that the equipment is treated by network applications as if it is not in the model. | SSH | 0..1 required (and =false) if equipment not in service, else no attribute
ConductingEquipment
Connector A conductor, or group of conductors, with negligible impedance, that serve to connect other conducting equipment within a single substation and are modelled with a single logical terminal.
p 7 "TABLE 1 - CIRCUIT DATA …S/S or Busbar Name" p 8 "TABLE 2 - TRANSFORMER DATA …S/S or Busbar Name" p 9 "TABLE 3 - LOAD INFORMATION …S/S or Busbar Name" p 10 "TABLE 4 - FAULT LEVEL INFORMATION …S/S or Busbar Name"
| BusBarSection | ipMax | Maximum allowable peak short-circuit current of busbar (Ipmax in IEC 60909-0). Mechanical limit of the busbar in the substation itself. Used for short circuit data exchange according to IEC 60909. | none (Basic)
Junction
EarthFaultCompensator
GroundingImpedance
PetersenCoil
Clamp
Ground
EquivalentEquipment
EquivalentBranch
EquivalentInjection
EquivalentShunt
ExternalNetworkInjection |  | with EnergySource?
StationSupply |  | with EnergySource?
assume there is no DC to deal with?

## XX RegulatingControl
Class | Parent Class or Class | Attribute | Description (CIM Notes) | LTDS Profile | LTDS UML Constraint | LTDS Additional Constraints | In CGMES 3.0 profile | In 61970-452 Ed4 EQ, SC, OP or 61970-456 Ed3 SSH profiles | In CIM information model | Comments / Questions | Existing LTDS requirement | Proposed GC0139 requirement
RegulatingControl
IdentifiedObject
| IdentifiedObject | description |  | Basic | 0..1
| IdentifiedObject | name |  | Basic | 1..1
PowerSystemResource
RegulatingControl Specifies a set of equipment that works together to control a power system quantity such as voltage or flow. Remote bus voltage control is possible by specifying the controlled terminal located at some place remote from the controlling equipment. The specified terminal shall be associated with the connectivity node of the controlled point. The most specific subtype of RegulatingControl shall be used in case such equipment participate in the control, e.g. TapChangerControl for tap changers. For flow control, load sign convention is used, i.e. positive sign means flow out from a TopologicalNode (bus) into the conducting equipment. The attribute minAllowedTargetValue and maxAllowedTargetValue are required in the following cases: - For a power generating module operated in power factor control mode to specify maximum and minimum power factor values; - Whenever it is necessary to have an off center target voltage for the tap changer regulator. For instance, due to long cables to off shore wind farms and the need to have a simpler setup at the off shore transformer platform, the voltage is controlled from the land at the connection point for the off shore wind farm. Since there usually is a voltage rise along the cable, there is typical and overvoltage of up 3 to 4 kV compared to the on shore station. Thus in normal operation the tap changer on the on shore station is operated with a target set point, which is in the lower parts of the dead band. The attributes minAllowedTargetValue and maxAllowedTargetValue are not related to the attribute targetDeadband and thus they are not treated as an alternative of the targetDeadband. They are needed due to limitations in the local substation controller. The attribute targetDeadband is used to prevent the power flow from move the tap position in circles (hunting) that is to be used regardless of the attributes minAllowedTargetValue and maxAllowedTargetValue.
| RegulatingControl | discrete | The regulation is performed in a discrete mode. This applies to equipment with discrete controls, e.g. tap changers and shunt compensators. | SSH | 1..1
| RegulatingControl | enabled | The flag tells if regulation is enabled. | none (SSH) | <is handled by RegulatingCondEq.controlEnabled>
| RegulatingControl | maxAllowedTargetValue | Maximum allowed target value (RegulatingControl.targetValue). | none (SSH)
| RegulatingControl | minAllowedTargetValue | Minimum allowed target value (RegulatingControl.targetValue). | none (SSH)
| RegulatingControl | mode | The regulating control mode presently available. This specification allows for determining the kind of regulation without need for obtaining the units from a schedule. | Basic | 1..1 =voltage
| RegulatingControl | monitoredPhase | Phase voltage controlling this regulator, measured at regulator location. | Basic | 1..1
| RegulatingControl | targetDeadband | This is a deadband used with discrete control to avoid excessive update of controls like tap changers and shunt compensator banks while regulating. The units of those appropriate for the mode. The attribute shall be a positive value or zero. If RegulatingControl.discrete is set to "false", the RegulatingControl.targetDeadband is to be ignored. Note that for instance, if the targetValue is 100 kV and the targetDeadband is 2 kV the range is from 99 to 101 kV. | SSH | 1..1 shall be zero or positive
| RegulatingControl | targetValue | The target value specified for case input. This value can be used for the target value without the use of schedules. The value has the units appropriate to the mode attribute. | SSH | 1..1
| RegulatingControl | targetValueUnitMultiplier | Specify the multiplier for used for the targetValue. | SSH | 1..1 =k

## XX TapChanger
Class | Parent Class or Class | Attribute | Description (CIM Notes) | LTDS Profile | LTDS UML Constraint | LTDS Additional Constraints | In CGMES profile | In 61970-45x profile | In CIM information model | Comments / Questions | Existing LTDS requirement | Proposed GC0139 requirement
RatioTapChanger
IdentifiedObject
| IdentifiedObject | description |  | Basic | 0..1 | [5 empty] | p 8 "TABLE 2 – TRANSFORMER DATA …Tap ..Minimum %" p 8 "TABLE 2 – TRANSFORMER DATA …Tap ..Maximum %" p 8 "4 The tapping range can be expressed as a percentage provided that the voltage base is clearly defined."
| IdentifiedObject | name |  | Basic | 1..1
PowerSystemResource
TapChanger Mechanism for changing transformer winding tap positions.
| TapChanger | controlEnabled | Specifies the regulation status of the equipment. True is regulating, false is not regulating. | SSH | 1..1
| TapChanger | ctRating | Built-in current transformer primary rating. | Basic | 0..1 required if lineDropCompensation=true, else no attribute | yes
| TapChanger | ctRatio | Built-in current transducer ratio. | Basic | 0..1 required if lineDropCompensation=true, else no attribute | yes
| TapChanger | highStep | Highest possible tap step position, advance from neutral. The attribute shall be greater than lowStep. | Basic | 1..1 shall be greater than lowStep
| TapChanger | InitialDelay | For an LTC, the delay for initial tap changer operation (first step change). | Basic | 0..1 required if associated TapChangeControl, else no attribute
| TapChanger | lowStep | Lowest possible tap step position, retard from neutral. | Basic | 1..1
| TapChanger | ltcFlag | Specifies whether or not a TapChanger has load tap changing capabilities. | Basic | 1..1
| TapChanger | neutralStep | The neutral tap step position for this winding. The attribute shall be equal to or greater than lowStep and equal or less than highStep. It is the step position where the voltage is neutralU when the other terminals of the transformer are at the ratedU. If there are other tap changers on the transformer those taps are kept constant at their neutralStep. | Basic | 1..1 shall be equal to or greater than lowStep and equal to or less than highStep
| TapChanger | neutralU | Voltage at which the winding operates at the neutral tap setting. It is the voltage at the terminal of the PowerTransformerEnd associated with the tap changer when all tap changers on the transformer are at their neutralStep position. Normally neutralU of the tap changer is the same as ratedU of the PowerTransformerEnd, but it can differ in special cases such as when the tapping mechanism is separate from the winding more common on lower voltage transformers. This attribute is not relevant for PhaseTapChangerAsymmetrical, PhaseTapChangerSymmetrical and PhaseTapChangerLinear. | Basic | 1..1
| TapChanger | normalStep | The tap step position used in "normal" network operation for this winding. For a "Fixed" tap changer indicates the current physical tap setting. The attribute shall be equal to or greater than lowStep and equal to or less than highStep. | none (Basic)
| TapChanger | ptRatio | Built-in voltage transducer ratio. | Basic | 0..1 required if lineDropCompensation=true, else no attribute | yes
| TapChanger | step | Tap changer position. Starting step for a steady state solution. Non integer values are allowed to support continuous tap variables. The reasons for continuous value are to support study cases where no discrete tap changer has yet been designed, a solution where a narrow voltage band forces the tap step to oscillate or to accommodate for a continuous solution as input. The attribute shall be equal to or greater than lowStep and equal to or less than highStep. | SSH | 1..1 shall be equal to or greater than lowStep and equal to or less than highStep
| TapChanger | subsequentDelay | For an LTC, the delay for subsequent tap changer operation (second and later step changes). | Basic | 0..1 required if TapChanger has associated TapChangeControl, else no attribute
RatioTapChanger A tap changer that changes the voltage ratio impacting the voltage magnitude but not the phase angle across the transformer. Angle sign convention (general): Positive value indicates a positive phase shift from the winding where the tap is located to the other winding (for a two-winding transformer).
| RatioTapChanger | stepVoltageIncrement | Tap step increment, in per cent of rated voltage of the power transformer end, per step position. When the increment is negative, the voltage decreases when the tap step increases. | Basic | 1..1
TapChangerControl
IdentifiedObject
| IdentifiedObject | description |  | Basic | 0..1
| IdentifiedObject | name |  | Basic | 1..1
PowerSystemResource
RegulatingControl Specifies a set of equipment that works together to control a power system quantity such as voltage or flow. Remote bus voltage control is possible by specifying the controlled terminal located at some place remote from the controlling equipment. The specified terminal shall be associated with the connectivity node of the controlled point. The most specific subtype of RegulatingControl shall be used in case such equipment participate in the control, e.g. TapChangerControl for tap changers. For flow control, load sign convention is used, i.e. positive sign means flow out from a TopologicalNode (bus) into the conducting equipment. The attribute minAllowedTargetValue and maxAllowedTargetValue are required in the following cases: - For a power generating module operated in power factor control mode to specify maximum and minimum power factor values; - Whenever it is necessary to have an off center target voltage for the tap changer regulator. For instance, due to long cables to off shore wind farms and the need to have a simpler setup at the off shore transformer platform, the voltage is controlled from the land at the connection point for the off shore wind farm. Since there usually is a voltage rise along the cable, there is typical and overvoltage of up 3 to 4 kV compared to the on shore station. Thus in normal operation the tap changer on the on shore station is operated with a target set point, which is in the lower parts of the dead band. The attributes minAllowedTargetValue and maxAllowedTargetValue are not related to the attribute targetDeadband and thus they are not treated as an alternative of the targetDeadband. They are needed due to limitations in the local substation controller. The attribute targetDeadband is used to prevent the power flow from move the tap position in circles (hunting) that is to be used regardless of the attributes minAllowedTargetValue and maxAllowedTargetValue.
| RegulatingControl | discrete | The regulation is performed in a discrete mode. This applies to equipment with discrete controls, e.g. tap changers and shunt compensators. | SSH | 1..1
| RegulatingControl | enabled | The flag tells if regulation is enabled. | none (SSH) | <is handled by TapChanger.controlEnabled>
| RegulatingControl | maxAllowedTargetValue | Maximum allowed target value (RegulatingControl.targetValue). | none (SSH)
| RegulatingControl | minAllowedTargetValue | Minimum allowed target value (RegulatingControl.targetValue). | none (SSH)
| RegulatingControl | mode | The regulating control mode presently available. This specification allows for determining the kind of regulation without need for obtaining the units from a schedule. | Basic | 1..1 =voltage
| RegulatingControl | monitoredPhase | Phase voltage controlling this regulator, measured at regulator location. | Basic | 1..1
| RegulatingControl | targetDeadband | This is a deadband used with discrete control to avoid excessive update of controls like tap changers and shunt compensator banks while regulating. The units of those appropriate for the mode. The attribute shall be a positive value or zero. If RegulatingControl.discrete is set to "false", the RegulatingControl.targetDeadband is to be ignored. Note that for instance, if the targetValue is 100 kV and the targetDeadband is 2 kV the range is from 99 to 101 kV. | SSH | 1..1 shall be zero or positive
| RegulatingControl | targetValue | The target value specified for case input. This value can be used for the target value without the use of schedules. The value has the units appropriate to the mode attribute. | SSH | 1..1
| RegulatingControl | targetValueUnitMultiplier | Specify the multiplier for used for the targetValue. | SSH | 1..1
TapChangerControl Describes behaviour specific to tap changers, e.g. how the voltage at the end of a line varies with the load level and compensation of the voltage drop by tap adjustment.
| TapChangerControl | lineDropCompensation | If true, the line drop compensation is to be applied. | Basic | 1..1
| TapChangerControl | lineDropR | Line drop compensator resistance setting for normal (forward) power flow. | Basic | 0..1 required if lineDropCompensation=true and forward line drop, else no attribute
| TapChangerControl | lineDropX | Line drop compensator reactance setting for normal (forward) power flow. | Basic | 0..1 required if lineDropCompensation=true and forward line drop, else no attribute
| TapChangerControl | maxLimitVoltage | Maximum allowed regulated voltage on the PT secondary, regardless of line drop compensation. Sometimes referred to as first-house protection. | Basic | 0..1
| TapChangerControl | minLimitVoltage | Minimum allowed regulated voltage on the PT secondary, regardless of line drop compensation. Sometimes referred to as last-house protection. | Basic | 0..1
| TapChangerControl | reverseLineDropR | Line drop compensator resistance setting for reverse power flow. | Basic | 0..1 required if lineDropCompensation=true and reverse line drop, else no attribute
| TapChangerControl | reverseLineDropX | Line drop compensator reactance setting for reverse power flow. | Basic | 0..1 required if lineDropCompensation=true and reverse line drop, else no attribute